## Error
ATTENTION:
The BEST Winery tool requires macros be enabled in Microsoft Excel in order to function.
Enabling Macros
BEST Winery uses macros to carry out many of the calculations and to make the program more user-friendly. During the process of opening a file, some versions of Excel ask whether the user wants to enable or disable macros, while others may automatically disable macros through a security setting. In order to use BEST Winery, the user must enable macros. If no dialogue box appeared asking you to enable or disable macros, select Tools --> Macro --> Security and click on medium or low. If medium security is chosen, every time BEST Winery is opened, a dialog box will appear asking the user if macros should be enabled or disabled.
Please close BEST Winery, open it again, and enable macros.

## BEST - Start
Acknowledgements
The University of Oregon Solar Radiation Monitoring Laboratory (UO SRML) adapted the BEST Winery software tool for Oregon with funding provided by the Oregon Department of Energy.
Many thanks to Gregory Jones of Southern Oregon University who provided climate data and information about the Oregon wine industry.
We extend our thanks to Christina Galitsky and Lawrence Berkeley National Laboratory, the creators of this software tool, for their assistance in adapting it for use in Oregon.
The original (California) version of this software contained the following notice:
"This work was supported by the Food Industry Energy Research (FIER) Grant Program of the Public Interest Energy Research Program (PIER) of the California Energy Commission (CEC), by CEC/CIEE Contract MR-0309 through the U.S. Department of Energy Contract under No. DE-AC03-76SF00098.
We would like to thank Patrick Healy and Susanne Zechiel of Fetzer Vineyards and Anthony Radspieler of Lawrence Berkeley National Laboratory who helped in the development of this tool and co-authored the accompanying Guidebook1. A special thanks to Scott Murtishaw who helped with much of the VBA programming to make BEST Winery run smoothly. Without their help, the development of this tool would not have been possible.
1 Galitsky, C., E. Worrell, A. Radspieler of Lawrence Berkeley National Laboratory, P. Healy and S. Zechiel of Fetzer Vineyards. BEST Winery Guidebook: Benchmarking and Energy and Water Savings Tool for the Wine Industry. LBNL 3184, May 2005."
Christina Galitsky and Ernst Worrell
Lawrence Berkeley National Laboratory

## Introduction (hidden)
BEST Winery
Integrated Benchmarking and Energy and Water Efficiency Assessment Tool for the Wine Industry
Lawrence Berkeley National Laboratory
Fetzer Vineyards
California Energy Commission
December 2006
Introduction
Oregon's rapidly growing wine industry is an increasingly important contributor to the state's economy. In 2005, Oregon was ranked third in the U.S. in total number of wineries, while wine output ranked fourth, based on the production of 1,591,300 cases of wine whose retail value was $184,700,000. Indirectly, wine production is estimated to account for more than $1.4 billion dollars in economic activity.
Given the accelerating pace of wine production in Oregon, we should expect that increasingly significant energy resources are being consumed by the state's winemaking industry. At present, this may represent as much as 5 GWh of electricity per year, as well as considerable amounts of fuel, including natural gas, LPG and propane.
Much of the electricity used in winemaking goes to refrigeration for cooling and cold storage. The rest is mainly used for compressed air, hot water or electricity for pumping and bottling line motors, though compressed air demand is highly variable from winery to winery. Enclosed areas for storage and processes also require lighting and many of these areas are cooled. Other non-process use power is required for buildings and other miscellaneous administrative or maintenance applications. Hot water is needed for cleaning barrels and equipment and for heating red wine ferments and yeast generator tanks.
The major water use areas are fermentation tanks, barrel washing, barrel soaking, bottling lines, cellars, and the crush pad. In efforts to conserve water, many wineries have begun to use treated wastewater to irrigate vineyards or landscaping, or may use it for frost protection, fire protection or dust abatement. Water use and disposal require pumping and heating which also increase energy costs.
Energy and water costs will probably continue to increase for wineries located in Oregon, making energy and water efficiency improvement an essential part of the business. Furthermore, excessive energy and water use result in considerable environmental damage. As a result, Oregon winemakers have begun to implement various efficiency measures, demonstrating an interest in adopting sustainable practices in viniculture and in their wineries.
Benchmarking can be a useful tool for understanding energy and water consumption patterns in an industrial facility and for designing policy to improve energy efficiency. Energy or water benchmarking for industry is a process in which the energy or water performance of an individual plant or an entire sector of similar plants is compared against a common metric that represents “standard” or “optimal” performance. It may also entail comparing the energy (or water) performance of a number of plants to each other. Because benchmark evaluation tools are used for comparison across a number of plants, there are two important characteristics they should have. First, because they are applied to plants or sectors of different sizes and outputs, the metric used should be irrespective of plant size. This is accomplished using intensity, which, for energy, measures energy use per unit of output. However, deciding how to measure units of output is not always clear. Second, the tool should be applicable to a wide range of facilities (in order to increase the robustness of the analysis) and, therefore, should be able to compensate for differences in production (such as tons of grapes received) at similar facilities.
While benchmarking provides insights into the relative energy and water performance of the plant, it is also a good starting point for analysis of additional improvement opportunities.
In designing an evaluation tool that compensates for production differences, it is necessary to take a look inside the production processes and account for the various process steps used. BEST Winery is based on this type of a process-step benchmarking approach. In this approach, the key process steps are identified and a benchmark performance is assigned to each step . The performance of your winery is then compared to a best or optimal winery, incorporating information about how each step is used by the winery. The performance of the winery is calculated and expressed as an Energy Intensity Indicator (EII) and a Water Intensity Indicator (WII). EII and WII are expressed relative to the benchmark.
BEST Winery also allows the user to evaluate on a preliminary basis the opportunities for energy and water efficiency improvement, to assess the impact on the performance of the facility, and to evaluate operation costs. This can help the user in developing a preliminary implementation plan for energy and water efficiency improvement.
The BEST Winery tool has been adapted for use in Oregon by the University of Oregon Solar Radiation Monitoring Laboratory (UO SRML), with funds provided by the Oregon Department of Energy. BEST Winery was developed originally by Lawrence Berkeley National Laboratory (LBNL) and Fetzer Vineyards, with financial support of the California Energy Commission (CEC). LBNL is a research laboratory of the U.S. Department of Energy managed by the University of California. LBNL develops tools and studies to reduce the environmental impact of energy use. Fetzer Vineyards in Hopland is one of the leading winemakers in the field of sustainable winemaking. Fetzer has pioneered the use of organic agricultural practices and renewable energy use in the wine industry.
Please read the manual on the next sheet or in the accompanying report before using BEST Winery.
For further information please contact:
For Oregon users:
Frank Vignola fev@uoregon.edu (541) 346-4745
For all others:
Christina Galitsky Cgalitsky@lbl.gov (510) 486 5137
Ernst Worrell Eworrell@lbl.gov 011-31-30-280-8374 (in the Netherlands)
Lynn Price LKPrice@lbl.gov (510) 486 6519

## Instructions (hidden)
BEST Winery
Integrated Benchmarking and Energy and Water Efficiency Assessment Tool for the Wine Industry
Lawrence Berkeley National Laboratory
Fetzer Vineyards
California Energy Commission
December 2006
Instructions
BEST Winery allows you to evaluate the energy and water efficiency of your winery by benchmarking energy and water intensity against an efficient reference winery. The reference winery is based on existing and proven practices and technologies. The reference winery simulates the production of the same products using the characteristics that you enter for your winery, however, using the most efficient technology. This will provide a score, called the Energy Intensity Index (EII) or Water Intensity Index (WII), which is a relative indication of the performance of your winery.
After evaluating the performance of your winery, you can evaluate the impact of selected energy-and water-efficiency measures by choosing the measures that you would likely introduce in your winery, or would like to evaluate for potential use. You select the degree or share of implementation for each of the measures, and BEST Winery will calculate the overall energy and water savings, cost savings, payback period and a re-calculated EII and WII.
Applicability
BEST Winery is designed for wineries that produce most wines (except for Champagne-like wines) and that have the tanks and barrels inside a building. Wineries that operate large outdoor tanks cannot use BEST Winery to evaluate the performance of that winery.
Computer Requirements
BEST Winery is designed for use in Excel using a PC with Windows 2000 or Windows XP.
After entering data please save BEST Winery with a different file name on your computer.
Using BEST Winery – step-by-step
An Excel workbook consists of a number of worksheets. Data from the input sheets is used for calculations throughout the workbook. After completing a worksheet, you will be automatically transferred to the next worksheet by pressing a button on the worksheet. In the following, we walk through the worksheets of BEST Winery step-by-step.
Input Sheet
In the Input Sheet you enter all essential information to enable benchmarking of your winery. BEST Winery assumes standard industry practices for fermentation and other process steps. If you wish to change these to simulate the practices at your winery, you must also fill in the worksheet "Optional Input”.
Only fill in the yellow cells! Cells with other colors are calculated from input data.
1. In the input sheet you first need to select the region where your winery is located and the region from which you source most of your grapes.
2. Secondly, you need to enter the annual production volumes of the different production steps in your winery, i.e. grapes received, juice received, total juice fermented, wine undergoing malolactic fermentation, amount of wine that is cold stabilized, amount of wine stored, total wine production, and total number of cases bottled onsite. BEST Winery distinguishes four types of wine, i.e. red, tank fermented dry whites, tank fermented sweet whites and barrel fermented white wine. Note that the unit for production volumes varies with the production step. Also note that the input is for a 12 month period. Wine stored should be based on capacity utilized on average throughout the 12 months, not the entire capacity of your storage rooms. There is a separate optional inventory sheet within the Input Worksheet that can help you calculate the amount of wine stored. (The numbers calculated will then have to be entered into cells C28 and F28, by you, separately).
3. Fill in the energy consumption separately for each fuel and electricity, as well as water. You also need to fill in the energy and water costs. Please fill these in for a full calendar year (12 months).
4. Two final boxes within the water data are required. Choose whether or not you treat your own wastewater onsite and whether or not you pump water from your own wells onsite. Answer yes or no from the drop-down menu.
5. When you fill in all the cells, press the “continue” button.
Optional Input
The Optional Input sheet allows you to tailor the production process of the reference winery to the production process of your winery. The sheet already contains default values, equal to values typical in most wineries. If you do not change the values in the yellow cells, the model will automatically use these values. If these values reflect or are close to your operating practices, there is no need to change them. If they do not, enter new numbers in the appropriate cells.
The table follows the production process of a winery, and allows you to change the data to reflect the operating conditions of your winery:
1. Enter the number of days and average number of hours/day that the receiving equipment is running.
2. Enter the number of days and average number of hours/day that the presses are running.
3. Enter the parameters of the building containing the fermentation tanks. Only enter the sizes of the cooled buildings. Please enter the sizes of the buildings/rooms for each of the wine types, or divide the space up over the wines if not processed in separate rooms or buildings. This information is used to calculate the cooling load of the building. The default value is based on a typical layout and tank distribution of a winery using tanks with approximately a 10 ft diameter and 18 ft. height.
4. For each wine type, enter the typical fermentation conditions, including fermentation temperature, fermentation time, sugar content of the juice, air exchange rate in the building (to remove CO2), as well as average tank dimensions.
5. For each wine type, enter the typical malolactic fermentation conditions. These are broken down into wines treated in tanks and those that undergo malolactic fermentation in barrels. Only barrel fermented white wines are assumed to undergo malolactic fermentation in the barrel. Other wines are assumed to undergo malolactic fermentation in tanks.
For tank fermented wines, enter: fermentation temperature, fermentation time, and average tank dimensions.
For barrel fermented wines, enter: fermentation temperature, fermentation time, and dimensions of the barrel room(s).
6. Cold stabilization is another key process demanding refrigeration. For each of the wine types, enter the typical stabilization conditions, including stabilization temperature, stabilization time, share of jacketed tanks, and tank dimensions.
7. Fill in the number of days that each type of wine undergoes fining.
8. For aging and storing in barrels, enter the room temperature at which the wine is stored in the cellar, as well as the cellar/barrel room dimensions. Fill in the temperatures for each of the barrel rooms/wine type. Enter the exchange rate if different than 1.
9. If you have a bottling plant (permanent or mobile), enter the number of weeks that the bottling line is run, and the number of hours per week it is typically in operation (on average).
10. By pressing on the button “Continue”, BEST Winery will calculate the energy and water intensity of your winery and compare these to the benchmark values. BEST Winery will open the results sheet.
Results
The results page will show the Energy Intensity Index (EII) and Water Intensity Index (WII). Once the actual energy intensity and benchmark energy intensity have been calculated, they can be used to construct an EII (and, similarly, a WII). The EII is a measurement of the total production energy intensity of your winery compared to a benchmark energy intensity. The EII can be used to calculate the energy-efficiency potential at your winery and it can be used for evaluating winery progress in energy efficiency improvement, by eliminating the effects of a change in product mix. The same applies to the WII and water.
The EII and WII can be used to calculate your winery efficiency potential by comparing your actual winery intensity to the intensity that would result if your winery used "reference" best technology for each process step. The difference between your actual intensity, which is the energy and water used at your winery per barrel or case produced, and that of the reference or benchmark winery, is calculated for each of the key process steps of the winery and then aggregated for the entire winery.
The EII or WII provides an indication of how the actual total production intensity of your winery compares to the benchmark or reference intensity. By definition, a winery that uses the benchmark or reference technology will have an EII or WII of 100. In practice, most wineries will have an EII and WII greater than 100. The gap between actual energy and water intensity at each process step and the reference level energy and water consumption can be viewed as the technical energy-efficiency potential or water-efficiency potential of your winery.
BEST Winery also provides an estimate of the potential for annual energy savings (both for electricity and fuel), energy costs savings, carbon dioxide (CO2) emission reduction, water, and water cost savings if your winery would perform at the same performance level as the benchmark or “reference” winery.
Press continue to see more detailed results, or to continue to evaluate opportunities available for energy and water efficiency in your winery.
Output Summary
The output summary sheet gives more detailed information about the benchmark winery and the calculations used to determine the EII and WII, as well as the efficiency potentials. It also shows emission factors used to calculate carbon and CO2 emissions reduction potentials.
To continue to evaluate your opportunities for energy and water-efficiency improvement, press the button “Continue”.
Evaluating Efficiency Opportunities
Once the EII has been calculated, BEST Winery can be used to preliminary evaluate the potential for energy and water efficiency improvement, by going through a menu of opportunities. The menu is broken into different energy and water uses:
- Water Efficiency (WE – Water)
- Energy Efficiency – Refrigeration (EE-Refrigeration)
- Energy Efficiency – Pumps (EE-Pumping)
- Energy Efficiency – Compressed Air (EE-Compressed air)
- Energy Efficiency – Motors (EE-Motors)
- Energy Efficiency – Lighting (EE-Lighting)
- Energy Efficiency – Hot Water and Heat Supply (EE-Hot Water)
- Energy Efficiency – Other Fuels (EE-Other_fuels)
- Energy Efficiency – Other Electric (EE-Other_electric)
- Energy Efficiency – Cogeneration (EE-CHP)
Each of the sheets contains a menu of efficiency opportunities, including typical energy and/or water savings, capital costs and payback period of that measure. You will need to specify the share of the total energy and water use used for that specific end-use to which the measure can still be applied, under "potential application".
By right-clicking on the cell with the measure name you can read a brief description of the specific measure. The information is also contained in the companion report. For each measure, typical energy or water savings, capital costs and payback period are provided. The measures span a wide range of applicability, both in system type and in design and operation, i.e. for new construction to maintenance. The estimates for energy or water savings and costs are necessarily based on past experiences in the wine and other industries; however, actual performance and very specific characteristics for the user’s winery may go beyond the capabilities of BEST and change the results. Hence, BEST gives an estimate of actual results for a preliminary evaluation of cost effective projects for the user’s winery; for a more detailed and exact assessment, a specialized engineer or contractor should be consulted.
The sheet will add the savings of the individual measures and provide a total savings estimate, as well as an average payback period. This information is transferred to the “ASSESSMENT RESULTS” sheet (see below).
In some sheets, e.g., lighting, pumping, motors, you have the ability to prepare an inventory of all lights, pumps or motors to help estimate the applicable share to which a measure can still be applied or to determine a more detailed estimate of energy use for that specific end use. You do not need to fill in the inventory, but it can help you to improve the estimate of the potential of efficiency improvement. If the inventory tables are not used, BEST Winery determines a typical energy use for that end-use (expressed as energy use per case of wine produced).
After selecting the efficiency measures and opportunities for each end-use, press the button “Continue”. This will open the next sheet with efficiency measures. The final "continue" button will open the Assessment Results Worksheet.
Assessment Results
The Assessment Results sheet provides the final results of the self-assessment of the potential for energy and water efficiency improvement.
The sheet will report the actual EII and WII, as well as what the EII and WII would be after all the selected energy and water-efficiency measures would be implemented.
It also reports on the technical potential (based on the EII and WII) and cost reductions, as were reported in the “RESULTS” sheet.
The sheet also summarizes the cumulative potential savings of the selected measures. BEST Winery provides an estimate of the annual energy and water savings, annual cost savings, cumulative capital costs, average payback period (of the selected package of measures) and reductions in CO2 emissions.
The saving and cost estimates are based on a survey of the literature and many projects. However, actual savings and costs will vary from project to project. BEST Winery is intended to help you select the most important or cost-effective projects for your winery, and to make a preliminary evaluation of these measures. Only a detailed assessment by a project engineer or a contractor can provide an exact estimate of the savings and costs of your specific project.
Press the button “Continue” to go to the ENERGY_RESULTS and WATER_RESULTS Worksheets.
ENERGY_RESULTS and WATER_RESULTS
BEST Winery provides three tables: 1) electricity measures you've selected; 2) fuel measures you've selected; and 3) water measures you've selected. These three tables contain all the measures that you have selected for each of those three categories, as well as estimated savings, costs and payback periods.
Pressing the "Continue" button on the ENERGY_RESULTS Worksheet will take you to the WATER_RESULTS Worksheet. The Continue button on the WATER_RESULTS Worksheet will take you to the References Worksheet.
References
The References Worksheet provides all references used in BEST Winery.
For questions please contact:
For Oregon users:
Frank Vignola fev@uoregon.edu (541) 346-4745
For all others:
Christina Galitsky Cgalitsky@lbl.gov (510) 486 5137
Ernst Worrell Eworrell@lbl.gov 011-31-30-280-8374 (in the Netherlands)
Lynn Price LKPrice@lbl.gov (510) 486 6519

## Input Sheet (hidden)
DATA INPUT SHEET
Please select the region in which your winery is located and the region from where most of the incoming grapes are grown.
Enter data in all yellow cells. To allow BEST Winery to benchmark your winery, all values must be entered.
Data should be entered for one specific calendar year.
Green cells are calculated and do not need to be entered.
| Site Parameters | [8 empty] | DO NOT CHANGE THESE CELLS!
BEST Winery will not work properly if they are changed!!
| Winery Region (select from list) | [8 empty] | Ashland
| Origin for the majority of your grapes (select from list). If grapes come from different regions, select the region that best represents most of your grapes | [8 empty] | 11.9
Optional Wine Storage Inventory
Enter the amount of wine you stored during each month of the year you are analyzing. Use the totals, below, to enter data into cells C28 & F28 on the left.
Wine Production Parameters
[8 empty] | Red | White
|  |  |  | Dry whites |  | Total | # of 50-Gal Barrels
| All inputs below should be given for the 12 month period being analyzed (e.g., the calendar year 2004). Fill in zeros where necessary. | Red | Sweet Whites | Tank fermented | Barrel fermented |  |  | % of barrels filled | % of barrels filled
| Grapes received over 12 month period (tons) |  |  |  |  | 0 | January
| Juice received over 12 month period (Gallons) |  |  |  |  | 0 | February
| Amount fermented over 12 month period (Gallons) |  |  |  |  | 0 | March
| Wine undergoing malolactic fermentation over 12 month period (Gallons) |  |  |  |  | 0 | April
| Wine undergoing malolactic fermentation over 12 month period (Cases) | 0 | 0 | 0 | 0 | 0
| Wine produced over 12 month period (Gallons) |  |  |  |  | 0 | May
| Wine produced over 12 month period (Cases) | 0 | 0 | 0 | 0 | 0
| Barrel room storage capacity utilized on average over 12 month period (Gallons) |  |  |  |  | 0 | June
| Wine stored in barrels over 12 month period (Cases) | 0 |  |  | 0 | 0
| Amount of wine that is cold stabilized over 12 month period (Gallons) |  |  |  |  | 0 | July
| Wine bottled over 12 month period (Cases) | [5 empty] | August
September
October
November
| Energy Data Required |  |  | Energy Billing Data |  |  | December
| Enter total amounts of each energy type for your 12 month period. Include all meters that supply energy used in wine production and related processes: |  |  | Enter Energy Billing data for your 12 month period (include all costs related to wine production): |  |  | Total Storage Capacity Utilized (Gallons) | 0 | 0
| Electricity consumption (kWh/year) |  |  | Electricity ($/year) |  |  |  | Enter these totals in Cells C28 and F28
| Natural gas consumption (therms/year) |  |  | Natural Gas ($/year)
| Annual propane consumption (gallons) |  |  | Propane ($/year)
| Annual fuel oil consumption - (MBtu/year) |  |  | Fuel Oil ($/year)
|  |  |  | Total |  | 0
Water Data Required
Enter total water consumed in 12 month period. Include all meters (or costs) that supply water to wine production and related processes:
Water consumption (gallons/year)
Water Billing ($/year)
0
Do you treat your own wastewater on site at this facility?
(type or select yes or no from drop down menu by clicking on cell)
Is the water used at your winery pumped from ground wells operated by your
winery? (type or select yes or no from drop down menu by clicking on cell)
yes
no
Note on B26: The amount of wine produced may be different than the amount of wine bottled for a variety of reasons, such as wine that is brought in from other facilities, wine that is produced at your winery but not bottled there, etc. Please enter in numbers for both production and wine bottled
Note on B28: Enter amount of wine stored on average over the 12 month period of analysis. You may use the inventory sheet on the right to help estimate total of each wine that is stored on a monthly basis (then averaged for the whole year). Please enter only the capacity that is utilized (on average), not the total number of barrels. Energy to clean and move empty barrels is accounted for elsewhere.
Note on B38: Enter all electricity that is used in wine production. This includes all electricity used in maintenance shops, administrative buildings and any other uses that are required to make, store and bottle wine.
Note on B39: Enter all natural gas that is used in wine production. This includes all natural gas used in maintenance shops, administrative buildings and any other uses that are required to make, store and bottle wine.
Note on B40: Enter all propane that is used in wine production. This includes all propane used in maintenance shops, forklifts, administrative buildings and any other uses that are required to make, store and bottle wine.
Note on B41: Enter all fuel oil that is used in wine production. This includes all fuel oil that is used in maintenance shops, administrative buildings and any other uses that are required to make, store and bottle wine.
Note on B48: Enter all water that is used in wine production. This includes all water that is used in maintenance shops, administrative buildings and any other uses that are required to make, store and bottle wine.

## Optional Input (hidden)
OPTIONAL INPUT DATA
This sheet contains default values for wine production parameters, shown in yellow.
These values can be changed to reflect operating parameters at your winery, or left unchanged so that the default values are used.
These cells do not need to be changed to benchmark your facility.
Green cells are calculated, but can be changed to reflect the layout of your winery.
Wine Production Parameters
Receiving
Time equipment runs annually (Days) | 60
Time equipment runs daily, on average, annually (hrs/day) | 15
Pressing
Time equipment runs annually (Days) | 60
Time equipment runs annually (hrs/day) | 15
Dry whites
Building Parameters - Winery/Tank Cellars | Red | Sweet Whites | Tank fermented | barrel fermented
Height (ft) | 26 | 26 | 26 | N/A
Outside Perimeter (ft) | 278 | 245 | 278 | N/A
Roof area (ft2) | 0 | 0 | 0 | N/A
Fermentation
Fermentation Temperature (ºF) | 77.5 | 49 | 59 | 56.5
Fermenting Temperature ( ºC) | 25.2778 | 9.4444 | 15 | 13.6111
Fermentation time (Days) | 8.5 | 28 | 14 | 7
Fermentation time (Hours) | 204 | 672 | 336 | 168
Sugar Content (Brix) | 24 | 21.5 | 23.5 | 23.5
Air Exchange Rate - CO2 Exhaust Fans (times/hour) | 6.875 | 7 | 6.8 | 6.8
Vessel dimensions - height (m) | 5.5 | 5.5 | 5.5 | N/A
- diameter (m) | 3.1 | 3.1 | 3.1 | N/A
Malolactic Fermentation
Fermentation or Room Temperature (ºF) | 70 | 70 | 70 | 78
Fermenting or Room Temperature ( ºC) | 21.1111 | 21.1111 | 21.1111 | 25.5556
Fermentation time (Days) | 45 | 56 | 56 | 56
Fermentation time (Hours) | 1080 | 1344 | 1344 | 1344
Barrel Fermentation: | MALOLACTIC FERMENTATION FOR REDS, SWEET WHITES AND TANK FERMENTED WHITES IS ASSUMED TO BE DONE IN TANKS
Room dimensions - average height (ft) |  |  |  | 24
- square footage |  |  |  | 7312.5
Tank Fermentation:
Vessel dimensions - height (m) | 5.5 | 5.5 | 5.5 | N/A
- diameter (m) | 3.1 | 3.1 | 3.1 | N/A
Cold Stabilization
Amount of wine that is cold stabilized (Gallons) | 0 | 0 | 0 | 0
Cold Stabilization Temp (ºF) | 26 | 26 | 26 | 26
Cold Stabilization Temp (ºC) | -3.3333 | -3.3333 | -3.3333 | -3.3333
Time (Days) | 35 | 35 | 35 | 35
Share Jacketed tanks (% of surface area) | 53% | 53% | 53% | 53%
Vessel dimensions - height (m) | 5.5 | 5.5 | 5.5 | 5.5
- diameter (m) | 3.1 | 3.1 | 3.1 | 3.1
Fining
Time (Days) | 112 | 112 | 112 | 112
Aging and Storing
Temperature of room (ºF) | 59 |  |  | 59
Temp of Room (ºC) | 15 |  |  | 15
Room dimensions - average height (ft) | 28 |  |  | 24
- square footage | 0 | TANK-FERMENTED |  | 0
Air change rate | 1 |  |  | 1
Bottling
Time equipment runs annually (Weeks) | 52
Time equipment runs annually (hrs/week) | 43.3333
Note on B13: Default given as 79 days. Enter another number or use this default.
Note on B14: Default given as 15 hours per day. Enter another number or use this default.
Note on B17: Default given as 79 days. Enter another number or use this default.
Note on B18: Default given as 15 hours per day. Enter another number or use this default.
Note on B23: Assuming benchmark perimeter is that of a square, we have scaled your winery's perimeter to your production in the following way: P= (1+W/W(best))*0.5*P(best) where P = perimeter of your winery's building W = wine production your winery W(best) = wine production benchmark P(best) = perimeter of benchmark's building
Note on B27: User may enter a fermenting temperature or use the default values already input.
Note on B28: ºC are automatically calculated from ºF entered in row above (or default values). If preferred, user may enter ºC here.
Note on B29: User may enter a fermenting time or use the default values already input.
Note on B30: Hours of fermentation are automatically calculated based on days entered above using 24 hours per day (or default values if no days were entered). If preferred, user can enter hours of fermentation here.
Note on B31: User may enter sugar content of the grapes or use the default values already input here.
Note on B33: User may enter vessel dimensions or use the default values already input here.
Note on B37: User may enter a fermenting temperature or use the default values already input.
Note on B38: ºC are automatically calculated from ºF entered in row above (or default values). If preferred, user may enter ºC here.
Note on B39: User may enter a fermenting temperature or use the default values already input.
Note on B40: Hours of fermentation are automatically calculated based on days entered above (or default values). If preferred, user can enter hours of fermentation here.
Note on B42: Only required for wines in which whole rooms are heated for malolactic fermentation.
Note on B43: Only required for wines in which whole rooms are heated for malolactic fermentation.
Note on B45: User may enter vessel dimensions or use the default values already input here.
Note on B50: User may enter a clarification temperature or use the default values already input.
Note on B51: ºC are automatically calculated from ºF entered in row above (or default values). If preferred, user may enter ºC here.
Note on B52: Default value given as the average of 4 to 6 weeks of cold stabilization.
Note on B54: User may enter vessel dimensions or use the default values already input here.
Note on B61: Room temperature only required for wines that are cooled in a room during storage.
Note on B62: ºC are automatically calculated from ºF entered in row above (or default values). If preferred, user may enter ºC here.
Note on B68: Default given as 365 days. Enter another number or use this default.
Note on B69: Default given as 40 hours per week for 7 months of the year and 48 hours per week for 5 months of the year (=43 per week on average). Enter another number or use this default.

## RESULTS (hidden)
BENCHMARKING - RESULTS
The results of benchmarking your facility to a "reference" best practice winery producing the same products under similar conditions are presented below. The results of the analysis are expressed as an intensity index. The performance (or index) of the "reference" facility is 100. The higher the intensity index the larger the potential for efficiency improvement.
| Energy Intensity Index (EII) | #NAME?
| Water Intensity Index (WII) | #NAME?
| Detailed Results |  |  | Summary Data
| Technical Potential for Efficiency Improvement: |  |  | Your Facility:
| Electricity (kWh saved/year) | -3194.1383 | #DIV/0! | Electricity Consumption (kWh/year) | 0
| Fuel (MBtu saved/year) | 0 | #DIV/0! | Fuel Consumption (MBtu/year) | 0
| Primary Energy (MBtu saved/year) | -23.6922 | #DIV/0! | Primary Energy Consumption (MBtu/year) | 0
|  |  |  | Energy Intensity (kBtu/case produced) | #DIV/0!
| Water (Gallons saved/year) | 0 | #DIV/0!
|  |  |  | Water Consumption (Gallons/year) | 0
|  |  |  | Water Intensity (Gallon/case) | #DIV/0!
Net Operation Cost Reduction:
| Electricity ($/year) | #DIV/0! | /year
| Fuel ($/year) | #DIV/0! | /year | Reference Facility:
| Energy - Total ($/year) | #DIV/0! | /year | Electricity Consumption (kWh/year) | 3194.1383
|  |  |  | Fuel Consumption (MBtu/year) | 0
| Water ($/year) | #DIV/0! | /year | Primary Energy Consumption (MBtu/year) | 23.6922
|  |  |  | Energy Intensity (kBtu/case produced) | #DIV/0!
| Total Cost Reduction ($/year) | #DIV/0! | /year
|  |  |  | Water Consumption (Gallons/year) | 0
|  |  |  | Water Intensity (Gallon/case) | #DIV/0!
CO2 Emission Reduction Potential:
| Total (metric ton CO2/year) | #DIV/0!
| Total (metric ton C/year) | #DIV/0!
Note on D24: These estimates include costs, that is, they are based on savings minus costs.
Note on F17: % of total electricity
Note on F18: % of total fuels
Note on F19: % of total primary energy

## Output_Summary (hidden)
DETAILED MODEL OUTPUT SUMMARY
Below are the summary data generated for the "reference best practice" winery by process step. These data are based on all production variables you entered in the Input Sheet.
| Red | White-sweet | White-tank | White-Barrel | Total
Pumping
Cooling water (kWh) |  |  |  |  | 0
Hot water malolactic (kWh) |  |  |  |  | 0
Hot water for cleaning - white bbl rm (kWh) |  |  |  |  | 0
Hot water for cleaning - red bbl rm (kWh) |  |  |  |  | 0
Hot water for cleaning - bottling (kWh) |  |  |  |  | 0
To/from waste/wells (kWh) |  |  |  |  | 0
Wine pumping (kWh) | 0 | 0 | 0 | 0 | 0
Wastewater aeration (kWh) |  |  |  |  | 0
Total pumping energy (kWh) | 0 | 0 | 0 | 0 | 0
Receiving
Unloading (kWh): | 0 | 0 | 0 | 0 | 0
Pumping & Moving (kWh): | 0 | 0 | 0 | 0 | 0
Total (kWh) | 0 | 0 | 0 | 0 | 0
Pressing
Pressing (kWh) | 0 | 0 | 0 | 0 | 0
Pumping (kWh) | 0 | 0 | 0 | 0 | 0
Total Pressing (kWh) | 0 | 0 | 0 | 0 | 0
Fermentation
Energy for heat of reaction (kJ) | 0 | 0 | 0 | 0 | 0
Energy for cooling incoming juice (kJ) | 0 | 0 | 0 | 0 | 0
Energy for conductive losses tank (kJ) | 0 | 0 | 0 | 0 | 0
Energy for conductive losses tank (kJ) | 0 | 0 | 0 | 0 | 0
Energy for cooling room (kJ) | 0 | 0 | 0 | 0 | 0
Infiltration losses (kJ) | 0 | 0 | 0 | 0 | 0
Energy for conductive losses - from walls (kJ) | -5414727.6147 | 10890227.0106 | 12357073.9141 | 0 | 17832573.31
Energy for conductive losses - from roof (kJ) | 0 | 0 | 0 | 0 | 0
Sub-Total Energy for fermentation (kJ) | -5414727.6147 | 7296452.0971 | 8279239.5224 | 0 | 10160964.0048
Coefficient of Performance (COP, W/W) | 4.1 | 4.1 | 4.1 |  | 0
Total Energy for fermentation (kJ) | -1320665.2719 | 1779622.4627 | 2019326.7128 | 0 | 2478283.9036
Total Energy for fermentation (kWh) | -366.8515 | 494.3396 | 560.9241 | 0 | 688.4122
Malolactic Fermentation
Energy for heating (MJ) | 0 | 0 | 0 | 0 | 0
Energy for conductive losses (MJ) | 0 | 0 | 0 | 0 | 0
Electricity use of fans (kWh) | 0 | 0 | 0 | 0 | 0
Total Fuel Use (MBtu) | 0 | 0 | 0 | 0 | 0
Total Electricity Use (kWh) | 0 | 0 | 0 | 0 | 0
Clarification & Stabilization
Cold Stabilization:
Energy for cooling tank (kJ) |  |  |  |  | 0
Energy for conductive losses tank (kJ) |  |  |  |  | 0
Energy for conductive losses tank (kJ) |  |  |  |  | 0
Energy for cooling room (kJ) |  |  |  |  | 0
Infiltration losses (kJ) |  |  |  |  | 0
Energy for conductive losses - from walls (kJ) |  |  |  |  | 0
Energy for conductive losses - from roof (kJ) |  |  |  |  | 0
Sub-Total Energy in Cold Stabilization (kJ) | 0 | 0 | 0 | 0 | 0
Coefficient of Performance (COP) | 3 | 3 | 3 | 3 | 3
Total Energy in Cold Stabilization (kJ) | 0 | 0 | 0 | 0 | 0
Fining:
Energy (kWh) | 0 | 0 | 0 | 0 | 2705.9962
Dialysis:
Energy (kWh) | 0 | 0 | 0 | 0 | 0
Total Energy Clarification & Stabilization (kWh) | 0 | 0 | 0 | 0 | 2705.9962
Aging & Storing
Total Energy used in Aging & Storing (kWh) | 0 | 0 | 0 | 0 | 0
Bottling
Energy used in equipment (kWh): |  |  |  |  | 0
Pumping Energy (kWh): |  |  |  |  | 0
Total Energy used in Bottling (kWh): |  |  |  |  | 0
Other
Lighting (kWh) |  |  |  |  | 0
Office Equipment, workshops (kWh) |  |  |  |  | 0
Miscellaneous (kWh) |  |  |  |  | 0
Hot water production (MBtu) |  |  |  |  | 0
Wine Heating before bottling (MBtu) |  |  |  |  | 0
Space heating and miscellaneous (MBtu) |  |  |  |  | 0
Propane for forklifts (MBtu) |  |  |  |  | 0
Total Electricity - Other (kWh) |  |  |  |  | 0
Total Fuels - Other (MBtu) |  |  |  |  | 0
Sub-Total Electricity (kWh) |  |  |  |  | 3394.4084
Below are additional reductions in energy use due to the measures listed. For a complete description of each measure, see the EE-Measures sheets.
Additional Energy Efficiency Corrections | % of total energy use | kWh
Energy Management Systems | 3% | 101.8323
Efficient Transformers | 0.9% | 30.5497
Power Factor Corrections | 2% | 67.8882
Values listed below were used to calculate the EII and WII for your facility, also listed below. They summarize the above data for the "reference best practice" winery and the data for your winery, entered by you in the Input Sheet.
Total Benchmark Electricity Use (kWh) |  |  |  |  | 3194.1383
Total Benchmark Fuel Use (MBtu) |  |  |  |  | 0
Total Benchmark Primary Energy Use (MBtu) |  |  |  |  | 23.6922
Benchmark Primary Energy Intensity (kBtu/case produced) |  |  |  |  | #DIV/0!
Total Benchmark Water Use (Gallons) |  |  |  |  | 0
Benchmark Water Intensity (gallon/case bottled) |  |  |  |  | #DIV/0!
Total Electricity Consumption at Your Winery (kWh) |  |  |  |  | 0
Total Fuel Consumption at Your Winery (MBtu) |  |  |  |  | 0
Total Primary Energy Use at Your Winery (MBtu) |  |  |  |  | 0
Primary Energy Intensity of Your Winery (kBtu/case produced) |  |  |  |  | #DIV/0!
Total Water Use at Your Winery (Gallons) |  |  |  |  | 0
Water Intensity at Your Winery (Gallon/case bottled) |  |  |  |  | #DIV/0!
EII-Electricity |  |  |  |  | 0
EII-Fuel |  |  |  |  | #DIV/0!
EII-Primary |  |  |  |  | 0
WII |  |  |  |  | #DIV/0!
Values below were calculated based on the tables above for the benchmark winery as well as those you entered in the Input Sheet for your winery.
Technical Potential | Energy | % | Costs ($) | CO2 (tCO2/year) | CO2 (tC/year)
Electricity (kWh) | -3194.1383 | #DIV/0! | #DIV/0! | -0.74423 | -0.20297
Fuel (MBtu) | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
Primary Energy (MBtu) | -23.6922 | #DIV/0!
Water (Gallons) | 0 | #DIV/0! | #DIV/0!
Total |  |  | #DIV/0! | #DIV/0! | #DIV/0!
Shares of Energy Use (below) are based on the "reference best practice" winery.
Share of Energy Use | Electricity | Fuel |  | Prices
Pumping (excl. cooling water) | 0%
Receiving | 0% |  |  | Electricity ($/kWh) | #DIV/0!
Pressing | 0% |  |  | Fuel ($/MBtu) | #DIV/0!
Fermentation | 21.55%
Malolactic fermentation | 0% | #DIV/0! |  | Water ($/Gallon) | #DIV/0!
Cold Stabilization/Clarification | 84.72%
Aging & Storage | 0%
Bottling | 0% | #DIV/0!
Other | 0% | #DIV/0!
Below are the emission factors used for Oregon and calculated for your winery.
Emission Factors
Coal | 25.74 | tC/TBtu | 94.38 | kgCO2/MBtu
Natural Gas | 14.47 | tC/TBtu | 53.0567 | kgCO2/MBtu
Propane | 17.2 | tC/TBtu | 63.0667 | kgCO2/MBtu
Oil | 19.95 | tC/TBtu | 73.15 | kgCO2/MBtu
Other (petcoke) | 27.85 | tC/TBtu | 102.1167 | kgCO2/MBtu
Winery specific fuel mix |  |  | #DIV/0! | kgCO2/MBtu
Electricity |  |  | 0.233 | kgCO2/kWh
PG&E average emission factor |  |  | 0.233 | kgCO2/kWh
Note on A108: This value is taken from the value you entered in the Input Sheet
Note on A109: This value is taken from the value you entered in the Input Sheet
Note on A110: This value is taken from the value you entered in the Input Sheet
Note on A111: Calculated from Fuel and Electricity Use you entered in Input Sheet
Note on A113: This value is taken from the value you entered in the Input Sheet
Note on A114: This value is calculated based on values you entered in the Input Sheet

## EE-Refrigeration (hidden)
REFRIGERATION
This Sheet lists potential refrigeration energy efficiency measures applicable to wineries in general. To determine the savings potential available at your winery, you need to
provide an indication of potential level of use of each of these measures in your winery considering the extent to which they have already been adopted. Do this by filling in
the column "potential application", below, as a percentage of possible applications within the specific area of refrigeration. Potential application here refers to only electricity
used in the applicable area of refrigeration, that is, fermentation, cold stabilization, aging & storage, and/or offices and miscellaneous cooling. (For a breakdown of
refrigeration energy use, see the inventory at the bottom of this sheet). Entering 100% means that you would like to adopt the measure wherever possible in your winery.
For example, entering 100% of caves for barrel storage would refer to 100% of the aging & storing energy.
#DIV/0!
Descriptions are accessed by scrolling your cursor over the cells in this column.
Share Refrigeration Use (of total electricity use): | 20.28% | #DIV/0! | kWh/case
Measures | Potential Application | Typical Energy Savings |  | Typical Investments | Total Energy Savings |  | Total Costs | Payback Period
|  | % of Refrigeration Energy Use | kWh/case |  | % of Refrigeration Energy Use |  |  |  | Notes
| (%) |  |  | $/kWh-saved |  | kWh/year | $ | years
System Changes
Trigeneration - Engine | 0% | 0% | 1.0632 | #DIV/0! | #DIV/0! | 0 | #DIV/0! | #DIV/0!
Trigeneration - Microturbine | 0% | 0% | 0.80534 | #DIV/0! | #DIV/0! | 0 | #DIV/0! | #DIV/0!
Reduce wattage lighting/occupancy control | #DIV/0! | 10% | #DIV/0! | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
Monitor performance | 0% | 3% | #DIV/0! | 0.48 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
Monitor refrigerant charge | 0% | 10% | #DIV/0! | 0.075 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
Monitor suction line filters | 0% | 3% | #DIV/0! | 0.015 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
Monitor contaminants in refrigerant | 0% | 2% | #DIV/0! | 0.1125 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
Tank insulation | 0% | 19.25% | #DIV/0! | 0.1882 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
Nighttime air cooling | 0% | 12.4% | #DIV/0! | 0.04 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
Reduced infiltration load from door closings | 0% | 15% | #DIV/0! | 0.015 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
Building Shell - reflective roofing materials | 0% | 3.45% | #DIV/0! | 0.74 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
Building & pipe Insulation and Vapor Barrier Integrity | 0% | 10% | #DIV/0! | 0.09 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
Size fan and motors more efficiently | 0% | 5% | #DIV/0! | 0.12 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
Electrodialysis | 0% | 34.32% | #DIV/0! | 4.16 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | When other benefits are taken into account, payback is less than one year.
Cave for barrel storage | 0% | 9% | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
Compressors
Control systems/Scheduling of compressors | 0% | 3% | #DIV/0! | 0.96 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
Floating Head Pressure (FHP) control versus fixed | 0% | 4% | #DIV/0! | 0.12 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
ASD/VFD on compressor motors | 0% | 10% | #DIV/0! | 0.32 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
Condensers
ASD/VFD on condenser fans | 0% | 5% | #DIV/0! | 0.18 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
Evaporators
Install automatic purgers on evaporative condensers | 0% | 5% | #DIV/0! | 0.71429 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
ASD/VFD on evaporator (air unit) fans | 0% | 4% | #DIV/0! | 0.2 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
Cycle evaporative (air unit) fans | 0% | 2% | #DIV/0! | 0.016 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
Total Potential Energy Savings | #DIV/0! | kWh/year
Total Investments | #DIV/0! | $
Total Average Payback Period | #DIV/0! | years
Refrigeration Inventory | % of Refrigeration Use |  | Optional Input: Estimating Investment Costs for Electrodialysis that include Wine Savings
Values are used to calculate % savings (column C, above) for some measures. Default values are given but may be changed.
| (Defaults given) |  | % Wine Saved: |  |  | 0.5%
Fermentation | 38% |  | Amount of Wine using Electrodialysis (Gallons): |  |  | 0
Cold Stabilization or Electrodialysis | 39% |  | Approximate $ per case of wine:
Aging/Barrel rooms | 9% |  | Approximate $ per gallon of wine: |  |  | 0
Cooling water pumping/circulation | 6% |  | $ saved per case of wine produced: |  |  | #DIV/0!
Cooling offices, miscellaneous | 14% |  | $ saved per kWh saved: |  |  | #DIV/0!
Total | 100%
|  |  | Typical investments, including wine saved: |  |  | #DIV/0!
Enter this number in Cell E 32, above
Note on A13: This number assumes your winery cold stabilizes your wine. If you use electrodialysis, this number should be reduced by about 8%.
Note on A19: The degree of application is selected in the EE-CHP sheet. The marginal costs are zero as the costs of the measure will have already been accounted in the CHP measure(s).
Note on A20: The degree of application is selected in the EE-CHP sheet. The marginal costs are zero as the costs of the measure will have already been accounted in the CHP measure(s).
Note on A21: Several energy efficiency measures relating to lighting are included on the Worksheet entitled EE-Lighting. In addition to the energy saved by reducing the electricity used in lighting, the reduction of lighting also reduces cooling load and refrigeration energy. Reduction of lighting is linked to lighting measures on the EE-Lighting sheet, where degree of application is selected. Because costs are already accounted for on the EE-Lighting sheet, marginal costs for this measure are zero. Costs for each of the lighting measures are included in the EE-Lighting Worksheet.
Note on A22: Automated monitoring of energy performance is not yet common but is very beneficial in quantifying the opportunity to address poor part-load efficiency of many systems, and in showing deterioration, such as effect of low refrigerant charge. The cost of automated monitoring is fixed relative to the size of the system and may be minor on a new system, where much of the data can be obtained from the control system. The monitoring system should have the ability to provide system and component level information to operating staff as well as high-level performance summaries for management (Scott, 2004). We estimate savings of 3% for the energy used in refrigeration by applying this measure.
Note on A23: Low refrigerant charge affects many small direct expansion (DX) systems, and can also exist without obvious indicators on larger flooded or recircirculation systems. Without this measure, the system will keep running until it can’t keep up any longer. This measure generally isn't applicable to large ammonia systems, but can be substantial if applicable and unnoticed. Scott (2004) estimates one in six DX systems has a low charge (or sometimes overcharge) situation sufficient to increase refrigeration energy usage by 20%. We conservatively estimate refrigeration savings of 10% wherever this measure is applied.
Note on A24: Monitor suction line filters. There are multiple reasons to monitor suction line filters. Debris will cause a pressure drop, but it is also important to know if anything is being carried out along with the returning vapor. If there is, there is most likely erosion occurring on the internal surface of the pipe which can lead to premature failure of the pipe. If debris is found, a corrosion rate testing program should be implemented (Dettmers, 2004). Generally this measure applies to smaller direct expansion (DX) systems, usually halocarbon not ammonia, although all systems can be monitored for unusual pressure drops that can originate from many sources (Scott, 2004). We estimate refrigeration systems savings from this measures to be about 3%.
Note on A25: Periodically monitor for contaminants (e.g., oil, water, etc.) to detect operating and maintenance problems with the system. We estimate refrigeration systems savings due to implementation of this measure to be 2%.
Note on A26: There are 3 primary types of tank insulation: Spray-on for large applications, foil over bubble wrap, and a rigid foam with an outer shell. Approximate energy savings generally vary from 20-33%, depending on the type of insulation system. We estimate, on average, refrigeration systems would save about 25% wherever this measure is implemented.
Note on A27: Bringing in outside air brings in air at lower temperatures and provides savings due to reduced cooling electricity use (due to lower air temperatures and less mechanical cooling) and larger electricity cost savings due to lower peak use. We estimate energy savings for this measure to be about 20%, applicable to warehouses (for aging and storing), offices and cold stabilization only, where outside air circulation is not already required. Fermentation already requires that fresh air is recirculated because of the CO2 generated within the fermentation process, so we do not include it here. Enter your application potential as a percentage of these areas.
Note on A28: Reduced infiltration load from door closings. Though proper door management and tight sealing doors, energy requirements for refrigeration will be reduced due to reductions in infiltration. Based on the BEST Winery model, undesired infiltration losses account for approximately 21% of refrigeration energy in fermentation and cold stabilization (Fresh air is required during indoor fermentation for worker safety due to the exhausted CO2 from the process. These air requirements are regulated and cannot be reduced. We estimate any additional infiltration to be undesired, and include only that air reduction in our model) . We assume 15% of the total refrigeration energy could be saved due to proper door management.
Note on A29: The building shell can serve as insulation from the weather (either hot or cold). The use of a reflective coating on the roof of buildings in sunny, hot climates like those found in California, can save on air conditioning costs inside. Two medical offices in Northern California used reflective roofs on their buildings and found summertime daily air-conditioning savings of 13 and 18% and reduced demand of 8 and 12% (Konopacki et al., 1998). Primary factors that influence energy savings include location, weather, roof insulation, air conditioning efficiency and building age. We estimate savings to be 15% on cooling requirements in aging and storing, as well as office buildings. Cooling requirements in aging and storing and office buildings is approximately 23% of total refrigeration energy. Parker and Barkaszi (1994) estimate the overall costs to be about $1 per square foot.
Note on A30: Building & pipe Insulation and Vapor Barrier Integrity. The integrity of insulation and vapor barriers may be inspected through the use of thermography. Replace degraded insulation and add insulation whenever possible. A thermographic camera can be used to see areas where the insulation has degraded, often because of moisture intrusion into the insulation. If the vapor barrier is broken, you will see water running down the walls or ice balls hanging from the point of rupture. Cost effectiveness of increasing insulation requires simulation, e.g., with 3Eplus software (Dettmers, 2004). We estimate refrigeration systems savings from this measure to be about 10%.
Note on A31: Motors and pumps that are sized inappropriately result in unnecessary energy losses. The same applies for fans and motors for the refrigeration system. Where peak loads can be reduced, motor and fan size can also be reduced. Correcting for motor over-sizing saves 1.2% of on the motor electricity consumption where applied (on average for the U.S. industry), and even larger percentages for smaller motors (Xenergy, 1998). It can be higher for individual motor systems. We assume similar savings for refrigeration re-sizing.
Note on A32: Electrodialysis uses selectively permeable membranes and an electric current to remove tartrates from wine that would generally otherwise undergo cold stabilization to remove these tartrates. Electrodialysis uses only about 12% of the energy used in cold stabilization, because no freezing and reheating is required (Dahlberg, 2004; Fetzer, 2004). In addition, reheating of wine after cold stabilization is no longer needed, saving yet more energy. Currently, replacement of the membranes required in electrodialysis is quite expensive, making operation costs about equal to the cost savings achieved by electricity reduction, when electricity is valued at about $0.10 per kWh (Dahlberg, 2004; Fetzer, 2004). However, WineSecrets, the major manufacturer of electrodialysis units in the U.S., claims savings achieved from wine that would be lost in cold stabilization make the process economical. They claim savings of 0.5% of wine, otherwise lost during cold stabilization. Currently, we have estimated costs to be $4.16/kWh saved, excluding savings from reduced wine loss. This number can be changed by the user, however, to account for savings due to reductions in wine loss to get a better estimate of payback period. Use the Optional Inventory Sheet below this box to calculate what the $/kWh saved should be (if including savings from less wine loss). The cost of $4.16 per kWh saved is for a large unit processing 3000 gallons per hour. A smaller winery may have lower first costs as well as a lower maintenance contract and a better payback period, as well. WineSecrets electrodialysis systems range from 400 gallons per hour for approximately $150,000, up to 3,000 gallons per hour for $ 800,000 (Dahlberg, 2004). In addition, A maintenance contract that includes membrane replacement, as well as other costs such as water, discharge, nitric acid, and operational labor costs between $0.025 and $0.055 per gallon, depending on the size of the unit.
Note on A33: Caves can be an alternative to above-ground buildings for wine storage. They provide an ideal environment for aging and storing wine, with almost constant temperatures year-round (typically about 60 degrees F) and a humidity of 80-90%. Some wineries have estimated a 7-year payback for digging a cave (Franson, 2000). Obviously, this payback is shorter for building new caves rather than for replacing an existing building. Magorian Mine Services estimate digging a cave typically costs around $100 per square foot, while concrete masonry block buildings typically cost $91 per square foot and super-insulated butler buildings cost $66 per square foot (Black, 2002). For our calculations, we use an average of these two types of buildings to estimate typical additional costs of building a cave. We estimate savings based on electricity used to cool a warehouse building, which are no longer required for caves.
Note on A35: Existing compressors generally have some controls but their computerized controls often only mimic electro-mechanical set points. Savings from this measure come from specific enhanced strategies and set points, such as optimizing compressor operation (if there are multiple parallel screw compressors) to reduce part-load inefficiency or floating suction set point (Scott, 2004). Baseloading with screw compressors and trimming with reciprocating compressors are generally recommended. Screw compressors should not be operated below 50% of design capacity while reciprocating compressors can go much lower (Dettmers, 2004). This measure could involve better control of parallel machines with standard feedback control or some sort of load forecasting scheme not done yet for refrigeration (Scott, 2004). We estimate refrigeration systems savings from this measure to be about 3%.
Note on A36: Floating Head Pressure (FHP) control versus fixed. Floating Head Pressure (FHP) involves additional fan power to reduce compressor power. This is a tradeoff, which means control method and relative power is important. Overall, this is the biggest opportunity for reducing the energy consumption o refrigeration compressors, at least on smaller systems. It is important not to allow head pressure to go too low. In ammonia refrigeration systems, certain processes in the system need a minimum head pressure. For example, liquid injection oil cooling often needs a minimum head pressure of around 135 psig. Other constraints may be needed for hot gas at a certain pressure/temperature to be able to meet defrost loads. Sometimes, lowering head pressure is simply an operational change, but often an additional compressor needs to be added to achieve it. In addition, there is a balance point in most systems when the extra energy added in fan power on the condenser exceeds the energy saved at the compressor (Dettmers). We estimate refrigeration systems savings from this measure to be about 4%.
Note on A37: Adjustable Speed Drives (ASDs)/Variable Frequency Drives (VFDs) on compressor motors. ASDs/VFDs used below a part-load ratio of approximately 0.95 on a screw compressor delivers equal capacity with lower electrical power requirements than a fixed speed compressor. At part-load ratio of 27%, the variable speed drive operation requires 40% less electrical power than the fixed speed case – each providing equal refrigeration capacity. Note that at full-load, the variable frequency drive is approximately 3% less efficient than the fixed speed drive case due to drive losses (Jekel, 2004b). We estimate refrigeration systems savings from this measure to be about 10%.
Note on A39: Adjustable Speed Drives (ASDs)/Variable Frequency Drives (VFDs) on condenser fans. From the standpoint of establishing a condenser operating strategy, the single greatest impact on energy efficiency is the choice of condenser fan capacity modulation. Prior to applying condenser fan ASDs/VFDs, it is important to evaluate the extent that the condensing (or head) pressure can be floated. Evaporative condenser operating strategies are dictated, in part, by the design of the connected refrigeration system and the selection of the condenser fan motor. The three most common strategies for condenser fan capacity control are: 1) on/off control with single-speed fans, 2) high/low/off control with 2-speed fans, 3) variable speed fans. (Jekel, 2004a). We estimate refrigeration system savings from this measure to be about 5%.
Note on A41: Automatic purgers are used to remove air and other non-condensables. On glycol/water chillers, it is recommended to purge air and other non-condensables from the system at least quarterly, possibly more during periods of heavy use (Dettmers, 2004). As a rule, 1% non-condensables could result in 1% efficiency loss, depending on the refrigerant used and the lift (Papar, 2004). We estimate refrigeration systems savings from this measure to be about 5%.
Note on A42: Adjustable Speed Drives (ASDs)/Variable Frequency Drives (VFDs) on evaporator (air unit) fans. ASDs/VFDs, continuous fixed speed (FS), and duty cycling (DC) represent three primary types of evaporator fan speed control strategies. Of the three, ASD/VFD has the best efficiency advantage at low part-load operating conditions, yet to be cost-effective there must be enough hours of part-load operation to “pay” for the drive (Jekel, 2004c). We estimate refrigeration systems savings from this measure to be about 4%.
Note on A43: Evaporator (air unit) fans should be cycled as permissible by the system (evaporator), but operated occasionally to prevent stratification of the air in the space. On certain types of evaporators (flooded & recirculated), fans should not be shut off until an extended period of solenoid off time is reached. Otherwise, it is possible to leave an evaporator sitting full of liquid ammonia. Stratification of the air means that the product(s) at the top of a warehouse could warm up beyond the specified temperature level and product(s) could be lost (Dettmers, 2004). Instead of shutting down the fan for various concerns (e.g., mold, start-up costs or lack of warning of need), a set-back mode may be used or a small dehumidifier coil/system may be installed for non-occupied modes. This measure requires integration with other system controls (Scott, 2004). We estimate refrigeration systems savings from this measure to be about 2%.
Note on A45: Total potential energy savings shown here do not include the trigeneration measures, as they are already included in the cogeneration worksheet.
Note on A46: Total investments shown here do not include the trigeneration measures, as they are already included in the cogeneration worksheet.
Note on C16: For measures which relate to only certain refrigeration energy uses, such as caves for barrel storage, energy savings are only applied to that section, using the inventory at the bottom of this Sheet. You may change the inventory at the bottom of the Sheet if known, to better reflect your winery. For measures that relate to all refrigeration energy, typical energy savings are applied to all refrigeration energy.
Note on E29: Reference: Home Energy Magazine Online May/June 1994. http://hem.dis.anl.gov/eehem/94/940509.html
Note on E32: Typical investments listed do not include the amount saved due to savings in wine losses. If savings from wine losses are to be included, you may enter another number here. We have included a table, below, to help you calculate what this number should be. Wine Secrets estimates that 0.5% wine is saved by using electrodialysis instead of cold stabilization. To estimate typical investments that include these savings, use the chart below. Copy number you calculate, below, into this cell when you are finished.

## EE-Pumping (hidden)
PUMPING
This Sheet lists potential pumping energy efficiency measures applicable to wineries in general. To determine the savings potential available at your winery, you need to
provide an indication of potential level of use of each of these measures in your winery considering the extent to which they have already been adopted. Do this by filling in
the column "potential application", below, as a percentage of possible applications for which you would like to use a given measure. Potential application here refers to only
electricity use used in pumping. Entering 100% means all pumping electricity, not 100% of energy or electricity use.
#DIV/0!
Descriptions are accessed by scrolling your cursor over the cells in this column.
Pumping Electricity Use: | 0% | #DIV/0! | kWh/case
The share of electricity use used for pumping purposes is calculated on the basis of the inventory (see below). If the inventory is not used, the default value given here is used.
Measures | Potential Application | Typical Energy Savings |  | Typical Investments | Total Energy Savings |  | Total Costs | Payback Period | Notes
|  | % of Motor Electricity Use |  |  | % of Motor Electricity Use
| (%) |  | kWh/case | $/kWh-saved |  | kWh/year | $ | years
Maintenance & Monitoring | 0% | 5% | #DIV/0! | 0.1 | 0% | #DIV/0! | #DIV/0! | #DIV/0!
Reduce Pumping Need | 0% | 7% | #DIV/0! | 0.5 | 0% | #DIV/0! | #DIV/0! | #DIV/0!
Controls | 0% | 30% | #DIV/0! | 0.11 | 0% | #DIV/0! | #DIV/0! | #DIV/0!
Correct Sizing of Pump | 0% | 20% | #DIV/0! | 0.12 | 0% | #DIV/0! | #DIV/0! | #DIV/0!
Correct Sizing of Piping | 0% | 0% | #DIV/0! | 0 | 0% | #DIV/0! | #DIV/0! | #DIV/0!
Efficient Pump Designs | 0% | 3.5% | #DIV/0! | 0.3 | 0% | #DIV/0! | #DIV/0! | #DIV/0!
Precision castings, coatings, polishings | 0% | 2.5% | #DIV/0! | 0.033 | 0% | #DIV/0! | #DIV/0! | #DIV/0!
Multiple Pumps | 0% | 15% | #DIV/0! | 0.3 | 0% | #DIV/0! | #DIV/0! | #DIV/0!
Trimming Impeller | 0% | 10% | #DIV/0! | 0.05 | 0% | #DIV/0! | #DIV/0! | #DIV/0!
Adjustable Speed Drive | 0% | 20% | #DIV/0! | 0.3 | 0% | #DIV/0! | #DIV/0! | #DIV/0!
Replace V-Belts | 0% | 4% | #DIV/0! | 0.1 | 0% | #DIV/0! | #DIV/0! | #DIV/0!
Total Potential Energy Savings | #DIV/0! | kWh/year
Total Investments | #DIV/0! | $
Total Average Payback Period | #DIV/0! | years
Pumping Inventory Sheet |  | Power | Total | Time | Electricity | Pumping Electricity
| Number Installed | Rating | Capacity | Use | Total Use
|  | (Watt) | (Watt) | (Hrs/year) | (kWh/year) | (%)
Receiving |  |  | 0 |  | 0 | N/A
Presses |  |  | 0 |  | 0 | N/A
Must Pump |  |  | 0 |  | 0 | N/A
Winery Pumps |  |  | 0 |  | 0 | N/A
Mobile Pumps |  |  | 0 |  | 0 | N/A
Cellars/Barrel rooms |  |  | 0 |  | 0 | N/A
Refrigeration/Cooling Circulation |  |  | 0 |  | 0 | N/A
Bottling |  |  | 0 |  | 0 | N/A
Water |  |  | 0 |  | 0 | N/A
Wastewater |  |  | 0 |  | 0 | N/A
Other |  |  | 0 |  | 0 | N/A
Other |  |  | 0 |  | 0 | N/A
Other |  |  | 0 |  | 0 | N/A
Other |  |  | 0 |  | 0 | N/A
Total (% here is % of total electricity in winery) |  |  |  |  | 0 | N/A
Note on A11: The share of electricity use used for pumping purposes is calculated on the basis of the inventory (see below). If the inventory is not used, the default value is used.
Note on A18: Inadequate maintenance at times lowers pump system efficiency, causes pumps to wear out more quickly and increases costs. Better maintenance will reduce these problems and save energy. Monitoring in conjunction with maintenance can be used to detect problems and determine solutions to create a more efficient system. Monitoring can determine clearances that need be adjusted, indicate blockage, impeller damage, inadequate suction, operation outside preferences, clogged or gas-filled pumps or pipes, or worn out pumps. Monitoring should include wear monitoring, vibration analyses for main pumps, pressure and flow monitoring, current or power monitoring, and distribution system inspection for scaling or contaminant build-up. Proper maintenance includes the following (Hydraulic Institute, 1994; LBNL et al., 1999): · Replacement of worn impellers, especially in caustic or semi-solid applications. · Bearing inspection and repair. · Bearing lubrication replacement, once annually or semiannually. · Inspection and replacement of packing seals. Allowable leakage from packing seals is usually between two and sixty drops per minute. · Inspection and replacement of mechanical seals. Allowable leakage is typically one to four drops per minute. · Wear ring and impeller replacement. Pump efficiency degrades from 1 to 6 points for impellers less than the maximum diameter and with increased wear ring clearances (Hydraulic Institute, 1994). · Pump/motor alignment check. Typical energy savings for monitoring and maintenance are estimated to be between 2 and 7% of pumping electricity. However, inefficient pumping systems may show higher savings. Paybacks are usually immediate to one year (Xenergy, 1998; US DOE/OIT, 2002a). We assume investments of $0.10/kWh-saved and savings of 5% of pumping energy use.
Note on A19: Holding tanks can be used to equalize the flow over the production cycle, enhancing energy efficiency and potentially reducing the need to add pump capacity. In addition, bypass loops and other unnecessary flows should be eliminated. Each of these steps saves 5 to 10% of pump system electricity consumption, on average for the U.S. industry (Easton Consultants, 1995). In smaller, new wineries, a design based on gravity can reduce the need for pumping by locating the tanks in such a way that no pumping is needed. The presses are located over the fermentation tanks, which are located over the storage facilities (cellar). It is also claimed that such a layout is easier on the grapes. Selected wineries are designed on the use of gravity, e.g. Byron (Santa Maria), Greystone (Napa), Niebaum-Coppola (Napa), Lemelson Winery (Oregon), and Willakenzie Estate (Oregon) (Hall, 1999). Due to costs, this practice is not recommended for existing wineries, but would be applicable to newly designed wineries if the local conditions allow such a design. Also, it may not be applicable to all kinds of wine (Hall, 1999). Several wineries specializing in Pinot Noir are using this technology where the grape needs a gentler knead. Hence, a gravity design may be most applicable to small, specialized wineries. The energy savings are estimated at 5-10% of total energy use in wineries. This investment is driven by wine quality and not by energy savings, and the additional investments (compared to a standard design) are strongly dependent on the site of the winery.
Note on A20: The objective of any control strategy is to shut off unneeded pumps or reduce load until needed. Remote controls enable pumping systems to be started and stopped more quickly and accurately when needed, and reduce the required labor. In 2000, Cisco Systems (CA) upgraded the controls on its fountain pumps that turn off the pumps during peak hours (CEC and US DOE/OIT, 2002). The wireless control system was able to control all pumps simultaneously from one location. The project saved $32,000 and 400,000 kWh annually, representing a savings of 61.5% of the fountain pumps’ total energy consumption. With a total cost of $29,000, the simple payback was 11 months. In addition to energy savings, the project reduced maintenance costs and increased the pumping system’s equipment life. Typical energy-efficiency improvement potential is estimated at 30% for control systems, with a specific investment of $0.11/kWh-saved.
Note on A21: Pumps that are sized inappropriately result in unnecessary losses. Where peak loads can be reduced, pump size can also be reduced. Correcting for pump oversizing saves 15 to 25% of electricity consumption for pumping (on average for the U.S. industry) (Easton Consultants, 1995). In addition, pump load may be reduced with alternative pump configurations and improved O&M practices. Where pumps are dramatically oversized, speed can be reduced with gear or belt drives or a slower speed motor. Paybacks for implementing these solutions are typically less than one year (US DOE/OIT, 2002). We estimate the typical savings at 20% with an investment of $0.12/kWh.
Note on A22: Similar to pumps, undersized pipes also result in unnecessary losses. The pipework diameter is selected based on the economy of the whole installation, the required lowest flow velocity, the minimum internal diameter for the application, the maximum flow velocity to minimize erosion in piping and fittings and plant standard pipe diameters. Increasing the pipe diameter may save energy but must be balanced with costs for pump system components. Easton Consultants (1995) and others in the pulp and paper industry (Xenergy, 1998) estimate retrofitting pipe diameters saves 5 to 20% of their energy consumption, on average for the U.S. industry. Energy savings and investments will depend strongly on the layout of the winery and site. Correct sizing of pipes should be done at the design or system retrofit stages where costs may not be restrictive. This measure is often not cost-effective in existing systems. Therefore, the measure is not included in this assessment, but should be considered in the design of a new facility.
Note on A23: According to inventory data, about 16% of pumps used in the U.S. are more than 20 years old. A pump's efficiency may degrade 10 to 25% in its lifetime (Easton Consultants, 1995). Newer pumps are 2 to 5% more efficient than older models. However, industry experts claim the problem is not necessarily the age of the pump but that the process has changed and the pump does not match the operation. Replacing a pump with a new efficient one saves between 2 to 10% of its energy consumption (Elliot, 1995). Higher efficiency motors have also been shown to increase the efficiency of the pump system 2 to 5% (Tutterow, 1999). A number of pumps are available for specific pressure head and flow rate capacity requirements. Choosing the right pump often saves both in operating costs and in capital costs (of purchasing another pump). For a given duty, selecting a pump that runs at the highest speed suitable for the application will generally result in a more efficient selection as well as the lowest initial cost (Hydraulic Institute and Europump, 2001). Exceptions to this include slurry handling pumps, high speed specified pumps or where the pump would need a very low minimum net positive suction head at the pump inlet.
Note on A24: The use of castings, coatings or polishing reduces surface roughness that, in turn, increases energy efficiency. It may also help maintain efficiency over time. This measure is more effective on smaller pumps. One case study in the steel industry analyzed the investment in surface coating on the mill supply pumps (350 kW pumps). They determined that the additional cost of coating, $1,200 (US) would be paid back in 5 months by energy savings of $2,700 (US) (or 36 MWh, 2%) per year (Hydraulic Institute and Europump, 2001). Energy savings for coating pump surfaces are estimated to be 2 to 3% over uncoated pumps (Best Practice Programme, 1998).
Note on A25: Often using multiple pumps is the most cost-effective and most energy-efficient solution for varying loads, particularly in a static head-dominated system. Installing parallel systems for highly variable loads saves 10 to 50% of the electricity consumption for pumping (on average for the U.S. industry) (Easton Consultants, 1995). Variable speed controls should also be considered for dynamic systems. Parallel pumps also offer redundancy and increased reliability.
Note on A26: If a large differential pressure exists at the operating rate of flow (indicating excessive flow), the impeller (diameter) can be trimmed so that the pump does not develop as much head. In the food processing, paper and petrochemical industries, trimming impellers or lowering gear ratios is estimated to save as much as 75% of the electricity consumption for that pump (Xenergy, 1998). In one case study in the chemical processing industry, the impeller was reduced from 320 mm to 280 mm, which reduced the power demand by more than 25% (Hydraulic Institute and Europump, 2001). Annual energy demand was reduced by 83 MWh (26%). With an investment cost of $390 (US), the payback on energy savings alone was 23 days. In addition to energy savings, maintenance costs were reduced, system stability was improved, cavitation reduced and excessive vibration and noise were eliminated. In another similar case study, Salt Union Ltd., the largest salt producer in the UK, trimmed the diameter of the pump impeller at its plant from 320 mm to 280 mm (13 to 11 inches) (Best Practice Programme, 1996b). After trimming the impeller, they found significant power reductions of 30%, or 197,000 kWh per year (710 GJ/year), totaling 8,900 GBP ($14,000 1994 US). With an investment cost of 260 GBP ($400 1993 US), and maintenance savings of an additional 3,000 GBP ($4,600 1994 US), this resulted in a payback of 8 days (11 days from energy savings alone). In addition to energy and maintenance savings, like the chemical processing plant, cavitation was reduced and excessive vibration and noise were eliminated. With the large decrease in power consumption, the 110 kW motor could be replaced with a 75kW motor, with additional energy savings of 58GJ (about 16,000 kWh) per year.
Note on A27: It is important to match the speed of the pump to the load requirement, because energy use is approximately proportional to the cube of the flow rate . Small reductions in flow that are proportional to pump speed may yield large energy savings. However, throttling valves should always be avoided. Extensive use of throttling valves or bypass loops may be an indication of an oversized pump (Tutterow et al., 2000). ASDs or variable speed drives or on/off regulated systems always save energy compared to throttling valves (Hovstadius, 2002). In addition, the installation of ASDs improves overall productivity, control and product quality, and reduces wear on equipment, thereby reducing future maintenance costs. According to inventory data collected by Xenergy (1998), 82% of pumps in U.S. industry have no load modulation feature (or ASD). Similar to being able to adjust load in motor systems, including modulation features with pumps is estimated to save between 20 and 50% of pump energy consumption, at relatively short payback periods, depending on pump size, load and load variation (Xenergy, 1998; Best Practice Programme, 1996a). As a general rule of thumb, unless the pump curves are exceptionally flat, a 10% regulation in flow should produce pump savings of 20% and 20% regulation should produce savings of 40% (Best Practice Programme, 1996a). Due to the wide variety of pump applications and hence variety in flows in a winery it is difficult to estimate typical savings. As a low estimate we assume efficiency improvements of 20% on all applicable pumps systems. The payback of installing an ASD depends strongly on the pump size and expected savings. Based on audits of wineries in California we assume an average investment of $0.3/kWh-saved.
Note on A28: Inventory data suggest 4% of pumps have V-belt drives, many of which can be replaced with direct couplings to save energy (Xenergy, 1998). Based on assessments in several industries, including wineries, savings are estimated at 4% . Investment costs are estimated at $0.10/kWh-saved with a simple payback period of 0.7-0.8 years.
Note on A49: Please add any other pumps not accounted for above
Note on A50: Please add any other pumps not accounted for above
Note on A51: Please add any other pumps not accounted for above
Note on A52: Please add any other pumps not accounted for above
Note on B15: Fill in the share of total pumping energy (see inventory below) to which you wish to apply the energy efficiency measure
Note on E15: Total typical investments, expressed as a function of annual energy savings

## EE-Compressed Air (hidden)
COMPRESSED AIR
Compressed air use is typically limited to the bottling facility, but may be found in other locations at well.
This Sheet lists potential energy efficiency measures for compressed air applicable to wineries in general. To determine the savings potential available at your winery,
you need to provide an indication of potential level of use of each of these measures in your winery considering the extent to which they have already been adopted. Do this
by filling in the column "potential application", below, as a percentage of possible applications for which you would like to use a given measure. Potential application here
refers to only electricity use used in compressed air systems. Entering 100% means all compressed air electricity, not 100% of energy or electricity use.
#DIV/0!
Descriptions are accessed by scrolling your cursor over the cells in this column.
Compressed Air Electricity Use: | 0% | #DIV/0! | kWh/case
The share of electricity use used for compressed air systems is calculated on the basis of the inventory (see below). If the inventory is not used the default value is based on the reference winery.
Measures | Potential Application | Typical Energy Savings |  | Typical Investments | Total Energy Savings |  | Total Costs | Payback Period | Notes
|  | % of Compressed Air Electricity Use |  |  | % of Compressed Air Electricity Use
| (%) |  | kWh/case | $/kWh-saved |  | kWh/year | $ | years
Maintenance & Monitoring | 0% | 15% | #DIV/0! | 0.06 | 0% | #DIV/0! | #DIV/0! | #DIV/0!
Repair Leaks | 0% | 20% | #DIV/0! | 0.04 | 0% | #DIV/0! | #DIV/0! | #DIV/0!
Reduce Pressure Drop | 0% | 3% | #DIV/0! | 0.035 | 0% | #DIV/0! | #DIV/0! | #DIV/0!
Reduce Compressed Air Usage | 0% | 15% | #DIV/0! | 0.14 | 0% | #DIV/0! | #DIV/0! | #DIV/0!
Controls | 0% | 12% | #DIV/0! | 0.25 | 0% | #DIV/0! | #DIV/0! | #DIV/0!
Reduce Inlet Temperature | 0% | 2% | #DIV/0! | 0.25 | 0% | #DIV/0! | #DIV/0! | #DIV/0!
Adjustable Speed Drives | 0% | 15% | #DIV/0! | 0.3 | 0% | #DIV/0! | #DIV/0! | #DIV/0!
Correct Sizing of Piping | 0% | 3% | #DIV/0! | 0.5 | 0% | #DIV/0! | #DIV/0! | #DIV/0!
Heat Recovery for Water Heating | 0% | 20% | #DIV/0! | 0.6 | 0% | #DIV/0! | #DIV/0! | #DIV/0!
Replace V-Belt Drives | 0% | 4% | #DIV/0! | 0.1 | 0% | #DIV/0! | #DIV/0! | #DIV/0!
Reduce Air Compressor Discharge Pressure | 0% | 8% | #DIV/0! | 0.0021 | 0% | #DIV/0! | #DIV/0! | #DIV/0!
Total Potential Energy Savings | #DIV/0! | kWh/year
Total Investments | #DIV/0! | $
Total Average Payback Period | #DIV/0! | years
Compressor Inventory Sheet |  | Power | Total | Time | Electricity
| Number Installed | Rating | Capacity | Use | Total Use | Share
|  | (Watt) | (Watt) | (Hrs/year) | (kWh/year) | (%)
Receiving |  |  | 0 |  | 0 | N/A
Presses |  |  | 0 |  | 0 | N/A
Winery |  |  | 0 |  | 0 | N/A
Winery |  |  | 0 |  | 0 | N/A
Cellars/Barrel rooms |  |  | 0 |  | 0 | N/A
Bottling |  |  | 0 |  | 0 | N/A
Other |  |  | 0 |  | 0 | N/A
Other |  |  | 0 |  | 0 | N/A
Other |  |  | 0 |  | 0 | N/A
Other |  |  | 0 |  | 0 | N/A
Total (% here is % of total electricity in winery) |  |  |  |  | 0 | N/A
Note on A12: The share of electricity use used for compressed air systems is calculated on the basis of the inventory (see below). If the inventory is not used the default value is based on the reference winery.
Note on A19: Inadequate maintenance can lower compression efficiency and increase air leakage or pressure variability, as well as lead to increased operating temperatures, poor moisture control, and excessive contamination. Improved maintenance and monitoring will reduce these problems and save energy. Proper maintenance includes the following (LBNL et al., 1998): • Regulators sometimes contribute to the biggest savings in compressed air systems. By properly sizing regulators, compressed air will be saved that is otherwise wasted as excess air. Also, it is advisable to specify pressure regulators that close when failing. • Keep the compressor and intercooling surfaces clean and foul-free. Blocked filters increase the pressure drop. By inspecting and periodically cleaning filters, the pressure drop may be kept low. Seek filters with just a 1 psig pressure drop over 10 years. The payback for filter cleaning is usually under 2 years (Ingersoll-Rand, 2001). Fixing improperly operating filters will also prevent contaminants from entering into tools and causing them to wear out prematurely. Generally, when pressure drop exceeds 2 to 3 psig, replace the particulate and lubricant removal elements, and inspect all systems at least annually. Also, consider adding filters in parallel that decrease air velocity, and, therefore, decrease air pressure drop. A 2% reduction of annual energy consumption in compressed air systems is projected for more frequent filter changing (Radgen and Blaustein, 2001). However, one must be careful when using coalescing filters; efficiency drops below 30% of design flow (Scales, 2002). • Keep motors properly lubricated and cleaned. Poor motor cooling can increase motor temperature and winding resistance, shortening motor life, in addition to increasing energy consumption. Compressor lubricant should be changed every 2 to 18 months and checked to make sure it is at the proper level. In addition to energy savings, this can help avoid corrosion and degradation of the system. • Inspect fans and water pumps for peak performance. • Inspect drain traps periodically to ensure they are not stuck in either the open or closed position and are clean. Some users leave automatic condensate traps partially open at all times to allow for constant draining. This practice wastes substantial energy and should never be undertaken. Instead, install simple pressure driven valves. Malfunctioning traps should be cleaned and repaired instead of left open. Some auto drains, such as float switch or electronic drains, do not waste air. Inspecting and maintaining drains typically has a payback of less than 2 years (Ingersoll-Rand, 2001). • Maintain the coolers on the compressor to ensure that the dryer gets the lowest possible inlet temperature (Ingersoll-Rand, 2001). • If using compressors with belts check belts for wear and adjust them. A good rule of thumb is to adjust them every 400 hours of operation. • Replace air lubricant separators according to specifications or sooner. Rotary screw compressors generally start with their air lubricant separators having a 2 to 3 psid pressure drop at full load. When this increases to 10 psid, change the separator (LBNL at al., 1998). • Check water-cooling systems for water quality (pH and total dissolved solids), flow, and temperature. Clean and replace filters and heat exchangers per manufacturer’s specifications. • Minimize leaks (see also Leaks section, below). • Specify pressure regulators that close when failing. • Check applications requiring compressed air for excessive pressure, duration or volume. Regulate these applications, either by production line sectioning or by pressure regulators on the equipment itself. Use a quality pressure regulator for tools that are not required to operate at maximum system pressure. Poor quality regulators tend to drift and lose more air. The unregulated tools operate at maximum system pressure at all times and waste excess energy. System pressures operating too high also result in shorter tool life and higher maintenance costs. Case studies demonstrated that the payback period for this measure would be shorter than half year (IAC, 2002). Proper monitoring includes the following: • Pressure gauges on each receiver or main branch line and differential gauges across dryers, filters, etc. • Temperature gauges across the compressor and its cooling system to detect fouling and blockages. • Flow meters to measure the quantity of air used. • Dew point temperature gauges to monitor the effectiveness of air dryers. • kWh meters and hours run meters on the compressor drive. • Compressed air distribution systems should be checked when equipment has been reconfigured to be sure no air is flowing to unused equipment or obsolete parts of the compressed air distribution system. • Check for flow restrictions of any type in a system, such as an obstruction or roughness. These require higher operating pressures than are needed. Pressure rise resulting from resistance to flow increases the drive energy on the compressor by 1% of connected power for every 2 psi of differential (LBNL et al., 1998; Ingersoll-Rand, 2001). Highest pressure drops are usually found at the points of use, including undersized or leaking hoses, tubes, disconnects, filters, regulators, valves, nozzles and lubricators (demand side), as well as air/lubricant separators, after-coolers, moisture separators, dryers and filters. • Check for compressed air use outside production hours. • Turn off unnecessary compressed air. Equipment that is no longer using compressed air should have the air turned off completely. This can be done using a simple solenoid valve (Scales, 2002). Check compressed air distribution systems when equipment has been reconfigured to be sure no air is flowing to unused equipment or obsolete parts of the compressed air distribution system.
Note on A20: Air leaks can be a significant source of wasted energy. A typical plant that has not been well maintained will likely have a leak rate equal to 20 to 50% of total compressed air production capacity (Ingersoll Rand, 2001; Price and Ross, 1989). Leak maintenance can reduce this number to less than 10%. Overall, a 20% reduction of annual energy consumption in compressed air systems is projected for fixing leaks (Radgen and Blaustein, 2001). The magnitude of a leak varies with the size of the hole in the pipes or equipment. A compressor operating 2,500 hours per year at 6 bar (87 psi) with a leak diameter of 0.02 inches (½ mm) is estimated to lose 250 kWh/year; 0.04 in. (1 mm) to lose 1100 kWh/year; 0.08 in. (2 mm) to lose 4,500 kWh/year; and 0.16 in. (4 mm) to lose 11,250 kWh/year (CADDET, 1997a). An Industrial Assessment Center (IAC) study shows the payback period for this measure is generally shorter than two months (IAC, 2002). In addition to increased energy consumption, leaks can make air tools less efficient, adversely affect production, shorten the life of equipment, and lead to additional maintenance requirements and increased unscheduled downtime. Leaks cause an increase in compressor energy and maintenance costs. The most common areas for leaks are couplings, hoses, tubes, fittings, pressure regulators, open condensate traps and shut-off valves, pipe joints, disconnects and thread sealants. The best way to detect leaks is to use an ultrasonic acoustic detector, which can recognize the high frequency hissing sounds associated with air leaks. After identification, leaks should be tracked, repaired and verified. Leak detection and correction programs should be ongoing efforts.
Note on A21: An excessive pressure drop will result in poor system performance and excessive energy consumption. Flow restrictions of any type in a system, such as an obstruction or roughness, require higher operating pressures than are needed. A pressure rise resulting from resistance to flow increases the drive energy on positive displacement compressors by 1% of connected power for each 2 psi of differential (LBNL et al., 1998; Ingersoll-Rand, 2001). Highest pressure drops are usually found at the points of use, including undersized or leaking hoses, tubes, disconnects, filters, regulators, valves, nozzles and lubricators (demand side), and air/lubricant separators on lubricated rotary compressors and after-coolers, moisture separators, dryers and filters (supply side). Minimizing pressure drop requires a systems approach in design and maintenance. Air treatment components should be selected with the lowest possible pressure drop at specified maximum operating conditions and best performance. Manufacturers’ recommendations for maintenance should be followed, particularly in air filtering and drying equipment, which can have damaging moisture effects like pipe corrosion. Finally, the distance the air travels through the distribution system should be minimized. An IAC study shows that the payback period is shorter than three months for this measure (IAC, 2002).
Note on A22: Turn off unnecessary compressed air. Equipment that is no longer using compressed air should have the air turned off completely. This can be done using a simple solenoid valve (Scales, 2002). Compressed air distribution systems should be checked when equipment has been reconfigured to be sure no air is flowing to unused equipment or obsolete parts of the compressed air distribution system. Use sources other than compressed air; many operations can be accomplished more economically and efficiently using energy sources other than compressed air. Some industry engineers believe this measure has the largest potential for compressed air energy savings. Various options exist to replace compressed air use, including: · Air motors should only be used for positive displacement. · Cooling electrical cabinets: air conditioning fans should be used instead of using compressed air vortex tubes. · Flowing high-pressure air past an orifice to create a vacuum: a vacuum pump system should be applied instead of compressed air venturi methods. · Cooling, aspirating, agitating, mixing, or package inflating: use blowers instead of compressed air · Cleaning parts or removing debris: brushes, blowers or vacuum pump systems or nozzles that are more efficient should be used instead of compressed air. · Moving parts: blowers, electric actuators or hydraulics should be used instead of compressed air. · Blowguns, air lances and agitation: low-pressure air should be used instead of high pressure compressed air. · Efficient electric motors for tools or actuators: electric motors should be considered because they are more efficient than using compressed air (Howe and Scales, 1995). Some, however, have reported motors can have less precision, shorter lives, and lack safety. In these cases, using compressed air may be a better choice. Numerous case studies in U.S. industries estimate an average payback period for replacing compressed air with other applications of 11 months (IAC, 2001).
Note on A23: Because of the large amount of energy consumed by compressors, whether in full operation or not, partial load operation should be avoided. For example, unloaded rotary screw compressors still consume 15 to 35% of full-load power while delivering no useful work (LBNL et al. 1998). Centrifugal compressors are cost effective when operated at high loads (Castellow et al., 1997). The objective of any control strategy is to shut off unneeded compressors or delay bringing on additional compressors until needed. All units that are on should be running at full-load, except for one. Positioning of the control loop is also important; reducing and controlling the system pressure downstream of the primary receiver can result in energy consumption of up to 10% or more (LBNL, et al., 1998). Energy savings for sophisticated controls are 12% annually (Radgen and Blaustein, 2001). Start/stop, load/unload, throttling, multi-step, variable speed and network controls are options for compressor controls and described below. Start/stop (on/off) is the simplest control available and can be applied to reciprocating or rotary screw compressors. For start/stop controls, the motor driving the compressor is turned on or off in response to the discharge pressure of the machine. They are used for applications with very low duty cycles. Applications with frequent cycling will cause the motor to overheat. Typical payback for start/stop controls is 1 to 2 years. Load/unload control, or constant speed control, allows the motor to run continuously but unloads the compressor when the discharge pressure is adequate. In most cases, unloaded rotary screw compressors still consume 15 to 35% of full-load power while delivering no useful work (LBNL et al., 1998). Hence, load/unload controls can be inefficient. Modulating or throttling controls allow the output of a compressor to be varied to meet flow requirements by closing down the inlet valve and restricting inlet air to the compressor. Throttling controls are applied to centrifugal and rotary screw compressors. Changing the compressor control from on/zero/off to a variable speed control can save up to 8% per year (CADDET, 1997b). Multi-step or part-load controls can operate in two or more partially loaded conditions. Output pressures can be closely controlled without requiring the compressor to start/stop or load/unload. System controls work on multiple compressors. Single master sequencing system controls take individual compressor capacities on- and off-line in response to monitored system pressure demand and shut down any compressors running unnecessarily. System controls for multiple compressors typically offer a higher efficiency than individual compressor controls.
Note on A24: If the airflow is kept constant, reducing the inlet air temperature reduces energy used by the compressor. In many plants, it is possible to reduce inlet air temperature to the compressor by taking suction from outside the building. As a rule of thumb, each 5°F (3°C) will save 1% compressor energy (CADDET, 1997a; Parekh, 2000). A payback period of 2 to 5 years has been reported for importing fresh air (CADDET, 1997a). In addition to energy savings, compressor capacity is increased when cold air from outside is used. Case studies taken from the IAC database have found an average payback period for importing outside air of shorter than 1.7 years (IAC, 2002).
Note on A25: Adjustable Speed Drives (ASDs) better match speed to load requirements for motor operations. There are various technologies to control the motor. The systems are offered by many suppliers and are available worldwide. Payback period may vary widely depending on the size of the motor system and use pattern. Implementing adjustable speed drives in rotary compressor systems can save 15% of the annual energy consumption (Radgen and Blaustein, 2001).
Note on A26: Inadequate pipe sizing can cause pressure losses, increase leaks and increase generating costs. Pipes must be sized correctly for optimal performance or resized to fit the current compressor system. Increasing pipe diameter typically reduces annual energy consumption by 3% (Radgen and Blaustein, 2001).
Note on A27: As much as 80 to 93% of the electrical energy used by an industrial air compressor is converted into heat. In many cases, a heat recovery unit can recover 50 to 90% of the available thermal energy for space heating, industrial process heating, water heating, makeup air heating, boiler makeup water preheating, industrial drying, industrial cleaning processes, heat pumps, laundries or preheating aspirated air for oil burners (Parekh, 2000). It’s been estimated that approximately 50,000 Btu/hour of energy is available for each 100 cfm of capacity (at full load) (LBNL et al., 1998). Paybacks are typically less than one year. Heat recovery for space heating is not as common with water-cooled compressors because an extra stage of heat exchange is required and the temperature of the available heat is lower. However, with large water-cooled compressors, recovery efficiencies of 50 to 60% are typical (LBNL et al., 1998). Implementing this measure saves up to 20% of the energy used in compressed air systems annually when waste heat is recovered for hot water preparation (Radgen and Blaustein, 2001).
Note on A28: Inventory data suggests 4% of pumps have V-belt drives, many of which can be replaced with direct couplings to save energy (Xenergy, 1998). Based on assessments in several industries, including wineries, savings are estimated at 4% . Investment costs are estimated at $0.10/kWh-saved with a simple payback period of 0.7-0.8 years.
Note on A29: Discharge pressure at the air compressor outlet should be minimized for each compressor in the winery. Savings and payback periods will vary greatly if a compressor is able to be taken offline due to these changes, however we estimate savings to be 8%, based on an audit performed at a California winery.
Note on A46: Please add any other pumps not accounted for above
Note on A47: Please add any other pumps not accounted for above
Note on A48: Please add any other pumps not accounted for above
Note on A49: Please add any other pumps not accounted for above
Note on B16: Fill in the share of total compressed air energy to which you wish to apply the energy efficiency measure
Note on E16: Total typical investments, expressed as a function of annual energy savings

## EE-Motors (hidden)
MOTORS
This Sheet lists potential motor energy efficiency measures applicable to wineries in general. To determine the savings potential available at your winery, you need to
provide an indication of potential level of use of each of these measures in your winery considering the extent to which they have already been adopted. Do this by filling
in the column "potential application", below, as a percentage of possible applications for which you would like to use a given measure. Potential application here refers to
only electricity use used in motor systems. Entering 100% means all motor electricity, not 100% of energy or electricity use.
#DIV/0!
Descriptions are accessed by scrolling your cursor over the cells in this column.
Motors Electricity Use: | 0% | #DIV/0! | kWh/case
The share of electricity use used for by motors is estimated on the basis of the inventory (see below), or on a default value derived from the reference winery.
Measures | Potential Application | Typical Energy Savings |  | Typical Investments | Total Energy Savings |  | Total Costs | Payback Period | Notes
|  | % of Motor Electricity Use |  |  | % of Motor Electricity Use
| (%) |  | kWh/case | $/kWh-saved |  | kWh/year | $ | years
Maintenance & Monitoring | 0% | 8% | 0 | 0.1 | 0% | #DIV/0! | #DIV/0! | #DIV/0!
Correct Sizing of Motor | 0% | 5% | 0 | 0.12 | 0% | #DIV/0! | #DIV/0! | #DIV/0!
High-Efficiency Motors | 0% | 7% | 0 | 0.35 | 0% | #DIV/0! | #DIV/0! | #DIV/0!
Adjustable Speed Drive | 0% | 20% | 0 | 0.3 | 0% | #DIV/0! | #DIV/0! | #DIV/0!
Replace V-Belts | 0% | 4% | 0 | 0.1 | 0% | #DIV/0! | #DIV/0! | #DIV/0!
Total Potential Energy Savings | #DIV/0! | kWh/year
Total Investments | #DIV/0! | $
Total Average Payback Period | #DIV/0! | years
Motor Inventory Sheet |  | Power | Total | Time | Electricity
Do not include motors used for pumps and refrigeration | Number Installed | Rating | Capacity | Use | Total Use | Share
|  | (Watt) | (Watt) | (Hrs/year) | (kWh/year) | (%)
Receiving |  |  | 0 |  | 0 | N/A
Presses |  |  | 0 |  | 0 | N/A
Winery - Ventilation Fans |  |  | 0 |  | 0 | N/A
Winery - Other |  |  | 0 |  | 0 | N/A
Cellars/Barrel rooms - Ventilation Fans |  |  | 0 |  | 0 | N/A
Cellars/Barrel rooms - Other |  |  | 0 |  | 0 | N/A
Bottling |  |  | 0 |  | 0 | N/A
Other |  |  | 0 |  | 0 | N/A
Other |  |  | 0 |  | 0 | N/A
Other |  |  | 0 |  | 0 | N/A
Other |  |  | 0 |  | 0 | N/A
Total (% here is % of total electricity in winery) |  |  |  |  | 0 | N/A
Note on A11: The share of electricity use used for by motors is estimated on the basis of the inventory (see below), or on a default value derived from the reference winery.
Note on A18: The purposes of motor maintenance are to prolong motor life and to foresee a motor failure. The maintenance measures can be categorized as preventive and predictive ones. The preventive measures, to avoid the unexpected downtime of motors, include electrical consideration, voltage imbalance, motor ventilation, alignment, lubrication, and load consideration. The predictive maintenance programs are to observe temperature, vibration, and other data for the determination of a time to overhaul or replace a motor (Barnish et al, 1997). The saving by conducting regular maintenance could range from 2% to 30% of total system energy use (EP, 2004).
Note on A19: Motors and pumps that are sized inappropriately result in unnecessary energy losses. Where peak loads can be reduced, motor size can also be reduced. Correcting for motor over-sizing saves 1.2% of motor electricity consumption applied (on average for the U.S. industry), and even larger percentages for smaller motors (Xenergy, 1998) and can be higher for individual motor systems.
Note on A20: High efficiency motors reduce energy losses through improved design, better materials, tighter tolerances and improved manufacturing techniques. With proper installation, energy-efficient motors run cooler and consequently have higher service factors, longer bearing and insulation life and less vibration. Typically, high efficiency motors are economically justified when exchanging a motor that needs replacement, but are not economically feasible when replacing a motor that is still working (CADDET, 1994; Price and Ross, 1989). Sometimes, though, according to case studies by the Copper Development Association (CDA, 2000), even working motor replacements can be beneficial. The payback period for individual motors varies based on size, load factor and running time. The best savings are achieved on motors running for long hours at high loads. When replacing retiring motors, payback periods are typically less than one year from energy savings alone (LBNL et al., 1998). The payback period is generally less than 3 years, depending on how long the motor is used. To be considered energy efficient in the U.S., a motor must meet performance criteria published by the National Electrical Manufacturers Association (NEMA). However, most manufacturers offer lines of motors that significantly exceed the NEMA-defined criteria, even those defined by NEMA as energy efficient (DOE, 2001). NEMA and other organizations are sponsoring a “Motor Decisions Matter” campaign to market NEMA-approved premium efficient motors to industry (NEMA, 2001). Even these premium efficiency motors can have a low payback period. It almost always makes sense not only to buy an energy efficient motor but also to buy the most efficient motor available (LBNL, 1998) when installing a new motor. Replacing a motor with a high efficiency motor is often a better choice than rewinding a motor. The practice of rewinding motors currently has no quality or efficiency standards. The efficiency of a motor decreases after rewinding. A standard consideration is a 2% drop in efficiency but this reduction could be as high as 20% to 25%. One case study shows that new motors are not only more energy efficient, but also able to reduce the overall operation cost (CDA, 2003). In addition, this would yield increased reliability. To avoid uncertainties in performance of the motor, a new high efficiency motor can be purchased instead of rewinding one. Several rewind rules are typically used for comparison of motors: (1) never rewind a motor damaged by excessive heat; (2) replace motors that are less than 100 horsepower and more than 15 years old; and (3) replace previously rewound motors.
Note on A21: Adjustable Speed Drives (ASDs) better match speed to load requirements for motor operations. There are various technologies to control the motor. The systems are offered by many suppliers and are available worldwide. Variable speed drives may be used for any industrial motor system that has variable loads. In wineries, these can be found in ventilation fans in the fermentation and barrel rooms, cooling tower fans, HVAC equipment, etc. Worrell et al. (1997) provide an overview of savings achieved with ASD in a wide array of applications and depended on the flow pattern and loads. The savings may vary between 7 and 60%. Payback period may vary widely depending on the size of the motor system and use pattern. Case studies of ASDs on cooling tower fans, ventilation equipment have demonstrated payback periods of around 2 years.
Note on A22: Inventory data suggests 4% of pumps have V-belt drives, many of which can be replaced with direct couplings to save energy (Xenergy, 1998). Based on assessments in several industries, including wineries, savings are estimated at 4% . Investment costs are estimated at $0.10/kWh-saved with a simple payback period of 0.7-0.8 years.
Note on A40: Please add any other motors not accounted for above
Note on A41: Please add any other motors not accounted for above
Note on A42: Please add any other motors not accounted for above
Note on A43: Please add any other motors not accounted for above
Note on B15: Fill in the share of total motors energy - not including motors used for pumps and refrigeration (see inventory below) to which you wish to apply the energy efficiency measure.
Note on E15: Total typical investments, expressed as a function of annual energy savings

## EE-Lighting (hidden)
LIGHTING
This Sheet lists potential lighting energy efficiency measures applicable to wineries in general. To determine the savings potential available at your winery, you need to
provide an indication of potential level of use of each of these measures in your winery considering the extent to which they have already been adopted. Do this by filling
in the column "potential application", below, as a percentage of possible applications for which you would like to use a given measure. Potential application here refers to
only electricity use used in lighting systems. Entering 100% means all lighting electricity, not 100% of energy or electricity use.
#DIV/0!
Descriptions are accessed by scrolling your cursor over the cells in this column.
Lighting Electricity Use (kWh): | 0% | #DIV/0! | kWh/case
The share of electricity use used for lighting purposes is calculated on the basis of the inventory (see below). If the inventory is not used, a default average is used.
Measures | Potential Application | Typical Energy Savings |  | Typical Investments | Total Energy Savings |  | Total Costs | Payback Period | Notes
|  | % of Lighting Electricity Use |  |  | % of Lighting Electricity Use
| (%) |  | kWh/case | $/kWh-saved |  | kWh/year | $ | years
Switch off lights when non-occupied | 0% | 100% | #DIV/0! | 0 | 0% | #DIV/0! | #DIV/0! | #DIV/0!
Replace Incandescents by CFLs | 0% | 65% | #DIV/0! | 0.2 | 0% | #DIV/0! | #DIV/0! | #DIV/0!
Replace Magnetic by Electronic Ballasts | 0% | 8% | #DIV/0! | 0.12 | 0% | #DIV/0! | #DIV/0! | #DIV/0!
Replace T-12 by T-8 Tubes | 0% | 15% | #DIV/0! | 0.25 | 0% | #DIV/0! | #DIV/0! | #DIV/0!
Replace HID-lights by T-5 Hi-Bay Lighting | 0% | 20% | #DIV/0! | 0.16 | 0% | #DIV/0! | #DIV/0! | #DIV/0!
Replace Mercury lights by High-Press Sodiums | 0% | 4% | #DIV/0! | 0.104 | 0% | #DIV/0! | #DIV/0! | #DIV/0!
Reduce Voltage of HID Lights | 0% | 15% | #DIV/0! | 0.3 | 0% | #DIV/0! | #DIV/0! | #DIV/0!
Replace Exit signs by LED exit Signs | 0% | 2% | #DIV/0! | 0.1 | 0% | #DIV/0! | #DIV/0! | #DIV/0!
Install Lighting controls | 0% | 10% | #DIV/0! | 0.15 | 0% | #DIV/0! | #DIV/0! | #DIV/0!
Install Daylighting | 0% | 14% | #DIV/0! | 0.5 | 0% | #DIV/0! | #DIV/0! | #DIV/0!
Total Potential Energy Savings | #DIV/0! | kWh/year
Total Investments | #DIV/0! | $
Total Average Payback Period | #DIV/0! | years
Lighting Inventory Sheet |  | Lamp | Total | Time | Electricity
| Number Installed | Rating | Capacity | Use | Total Use | Share
|  | (Watt) | (Watt) | (Hrs/year) | (kWh/year) | (%)
Incandescent |  |  | 0 |  | 0 | N/A
Incandescent |  |  | 0 |  | 0 | N/A
Fluorescent - T12 |  |  | 0 |  | 0 | N/A
Fluorescent - T12 |  |  | 0 |  | 0 | N/A
Fluorescent - T8 |  |  | 0 |  | 0 | N/A
Fluorescent - T8 |  |  | 0 |  | 0 | N/A
Hi-Bay - HID |  |  | 0 |  | 0 | N/A
Hi-Bay - T5 |  |  | 0 |  | 0 | N/A
Hi-Bay - mercury |  |  | 0 |  | 0 | N/A
Fluorescent Exit signs |  |  | 0 |  | 0 | N/A
LED Exit signs |  |  | 0 |  | 0 | N/A
Other |  |  | 0 |  | 0 | N/A
Other |  |  | 0 |  | 0 | N/A
Other |  |  | 0 |  | 0 | N/A
Other |  |  | 0 |  | 0 | N/A
Total |  |  |  |  | 0 | N/A
Calculation Share Switch-off Lights | Current Time | Potential time lights could be turned off | Switch-off
| Use |  | Share | Notes
| (hours/year) | (hours) | (%)
Incandescent | 0 |  | 0%
Incandescent | 0 |  | 0%
Fluorescent - T12 | 0 |  | 0%
Fluorescent - T12 | 0 |  | 0%
Fluorescent - T8 | 0 |  | 0%
Fluorescent - T8 | 0 |  | 0%
Hi-Bay - HID | 0 |  | 0%
Hi-Bay - T5 | 0 |  | 0%
Hi-Bay - mercury | 0 |  | 0%
Fluorescent Exit signs | 0 |  | 0%
LED Exit signs | 0 |  | 0%
Other | 0 |  | 0%
Other | 0 |  | 0%
Other | 0 |  | 0%
Other | 0 |  | 0%
Total (% here is % of total electricity in winery) |  |  | 0%
Note on A11: The share of electricity use used for lighting purposes is calculated on the basis of the inventory (see below). If the inventory is not used, a default average is used.
Note on A18: An energy management program that aims to improve the awareness of personnel with regard to energy use can help to switch off lights and other equipment when not in use. For calculation of share see below. The result of the table below is automatically copied.
Note on A19: The fluorescent lamp lasts roughly ten times longer than an incandescent light and is three times more effective in lighting provided. Typical energy savings are 50-75% per lamp. The payback period for the replacement varies with the number of hours that the lamps are used, but can be as low as five months. We estimate the typical investments at $0.20/kWh-saved. The Benziger family Winery (170,000 cases) replaced incandescent lamps by CFL in 2002, and reduced the total electricity bill for lighting by 25% (Wine Institute, 2002).
Note on A20: A ballast is a mechanism that regulates the amount of electricity required to start a lighting fixture and maintain a steady output of light. Electronic ballasts save 12-30% power over their magnetic predecessors (Cook, 1998; EPA, 2001). New electronic ballasts have smooth and silent dimming capabilities, in addition to longer lives (up to 50% longer), faster run-up times and cooler operation (Eley et al., 1993; Cook, 1998). New ballasts also have automatic switch-off for faulty or end of life lamps. We assume 25% typical savings when replacing a magnetic ballast by an electronic ballast. Total energy savings will depend on the number of magnetic ballasts still in use in the winery. Typical energy savings are estimated at 8% of total electricity use for lighting. The typical investments are estimated at $0.12/kWh-saved.
Note on A21: T-12 refers to the diameter in 1/8-inch increments (T-12 means 12/8 inch or 3.8 cm diameter tubes). The initial output for T-12 lights is high, but energy consumption is also high. They also have extremely poor efficacy, lamp life, lumen depreciation and color rendering index. Because of this, maintenance and energy costs are high. Replacing T-12 lamps with T-8 lamps (smaller diameter) approximately doubles the efficacy of lighting. Also, T-8 tubes generally last 60% longer than T-12 tubes saving maintenance costs. Typical energy savings from the replacement of a T-12 by a T-8 are around 30%. Based on experiences with several industrial facilities, the investment costs for replacing T-12 by T-8 and electronic ballasts are estimated at $0.25-0.30/kWh-saved. It is important to remember, however, to work both with the suppliers and manufacturers on the system as a whole through each step of the process. There are a number of T-8 lights and ballasts and the correct combination should be chosen for each system. The Gillette Company manufacturing facility in Santa Monica, California replaced 4300 T-12 lamps with 496 metal halide lamps in addition to replacing 10 manual switches with 10 daylight switches (EPA, 2001). They reduced electricity by 58% and saved $128,608 annually. The total project cost was $176,534, producing a payback period of less than 1.5 years.
Note on A22: HID lights are typically used in large production spaces and loading docks. Traditional HID lighting can be replaced with high-intensity fluorescent lighting. These new systems incorporate high-efficiency fluorescent lamps (T-5), electronic ballasts and high-efficacy fixtures that maximize output to the workspace. Advantages of the new system are many: lower energy consumption, lower lumen depreciation over the lifetime of the lamp, better dimming options, faster start-up and restrike capability, better color rendition, higher pupil lumens ratings and less glare (Martin et al., 2000). High-intensity fluorescent systems yield 50% electricity savings over standard metal halide HID. Dimming controls that are impractical in the metal halide HIDs can also save significant energy in the new system. Retrofitted systems cost about $185 per fixture, including installation costs (Martin et al., 2000). Specific investments are estimated at $0.16/kWh-saved. In addition to energy savings and better lighting qualities, high-intensity fluorescents can help improve productivity and have reduced maintenance costs.
Note on A23: In industries where color rendition is critical, metal halide lamps save 50% compared to mercury or fluorescent lamps (Price and Ross, 1989). Where color rendition is not critical, high pressure sodium lamps offer energy savings of 50 to 60% compared to mercury lamps (Price and Ross, 1989). High pressure sodium and metal halide lamps also produce less heat, reducing HVAC loads. In addition to energy reductions, the metal halide lights provide better lighting, provide better distribution of light across work surfaces, improve color rendition and reduce operating costs (GM, 2001).
Note on A24: Reducing system voltage can also save energy. Toyota put in reduced voltage HID-lights and found a 30% reduction in lighting (Toyota, 2002). There are commercial products on the market that attach to a central panel switch (controllable by computer) and constricts the flow of electricity to fixtures, thereby reducing voltage and saving energy, with an imperceptible loss of light. Voltage controllers work with high intensity discharge (HID) and fluorescent lighting systems. Various systems are on the market, e.g., EnergySaver, Wattman and others. Energy savings will depend on the number of hours that a light is used. Energy savings will vary between 15 and 35%. We estimate typical energy savings at 13% of lighting energy use in a winery. The investment costs depend on the size of the lighting system and number of controllers needed. A single voltage controller unit can be used with up to 400 lighting fixtures, depending on the size of the unit and the distance between fixtures. Prices for the units vary, from $500 to $15,000 (2000 prices), depending on the electrical load. Typical payback for lights that are used 24 hours/day is less than one year. We assume typical costs of $0.30/kWh-saved.
Note on A25: Energy costs can be reduced by switching from incandescent lamps to LEDs or radium strips in exit sign lighting. An incandescent exit sign uses about 40W, while LED-signs may use about 4-8W, reducing electricity use by 80-90%. A 1998 Lighting Research Center survey found that about 80 percent of exit signs being sold use LEDs (LRC, 2001). The lifetime of a LED exit sign is about 10 years, compared to one year for incandescent signs, reducing maintenance costs considerably. In addition to exit signs, LEDs are increasingly being used for path marking and emergency wayfinding systems. Their long life and cool operation allows them to be embedded in plastic materials, which makes them perfect for these applications (LRC, 2001). A new LED-exit sign costs about $20-30/piece. Kits are sold to retrofit the lamps in existing exit signs for similar prices. The payback period can be as low as 6 months. EPA’s ENERGY STAR program provides a list of suppliers of LED exit signs. An alternative is the Tritium exit sign that is self-luminous, and do not need any power supply. The lifetime of these signs is estimated at about 10 years, while the costs are $200/piece or more. The high capital costs make this type of sign attractive for new construction or if no power supply is available.
Note on A26: Lights can be shut off during non-working hours by automatic controls, such as occupancy sensors, which turn off lights when a space becomes unoccupied. Manual controls can also be used in addition to automatic controls to save additional energy in small areas. Other lighting controls include daylight controls for indoor and outdoor lights, including HID-lights used in loading bays and other production space. Occupancy sensors can save up to 10 or 20% of the lighting energy use. Savings are estimated at 2.4% of total electricity use for lighting at a typical winery facility. Numerous case studies throughout the United States indicate average payback period for lighting controls is approximately 1.1 years. Based on the assessments we estimate the total costs (including installation) at $0.15/kWh-saved.
Note on A27: Daylighting is the efficient use of natural light in order to minimize the need for artificial light in buildings. Increasing levels of daylight within rooms can reduce electrical lighting loads by up to 70% (Caddet, 2001). Unlike conventional skylights, an efficient daylighting system may provide evenly dispersed light without creating heat gains. The reduced heat gains will reduce the need for cooling compared to skylights. Daylighting differs from other energy efficiency measures because its features are integral to the architecture of a building, and so is applied primarily to new buildings and incorporated at the design stage. However, existing buildings can be cost-effectively refitted with daylighting systems. Various daylighting systems are available on the market; some of which can be supplied as kits to retrofit an existing building. Daylighting can be combined with lighting controls to maximize its benefits. Because of its variability, daylighting is almost always combined with artificial lighting to provide the necessary illumination on cloudy days or after dark. Daylighting technologies include properly placed and shaded windows, atria, angular or traditional (flat) roof lights, clerestories, light shelves and light ducts. Clerestories, light shelves and light ducts utilize angles of the sun and redirect light with walls or reflectors. Not all parts of the winery may be suitable for the application of daylighting. Daylighting is most appropriate for those areas that are used in daytime hours by people. This may include parts of the winery, bottling facility, offices, tasting room and parts of the warehouses. Lighting in office and similar spaces may consume as much as 2% of total winery electricity use. In office spaces, daylighting may save between 30 and 70% (Caddet, 2001). The savings will vary widely depending the facility and buildings. As general guidance we estimate the typical savings on 14% of total lighting electricity use in a typical facility. Various companies offer daylighting technologies. More information on daylighting can be found at the website of the Daylighting Collaborative led by the Energy Center Wisconsin (http://www.daylighting.org/). Daylighting systems will have a payback period of around 4 years, although shorter paybacks have been achieved. We estimate typical investments at $0.50/kWh-saved.
Note on A49: Please add any other lighting applications not mentioned above, e.g. perimeter lighting
Note on A50: Please add any other lighting applications not mentioned above, e.g. perimeter lighting
Note on A51: Please add any other lighting applications not mentioned above, e.g. perimeter lighting
Note on A52: Please add any other lighting applications not mentioned above, e.g. perimeter lighting
Note on B15: Fill in the share of total lighting energy (see inventory below) to which you wish to apply the energy efficiency measure
Note on C56: Enter number off hours that lights can be switched off for each category
Note on D74: Result is automatically entered in measure table above
Note on E15: Total typical investments, expressed as a function of annual energy savings

## EE-Hot Water (hidden)
HOT WATER SUPPLY (BOILER)
This Sheet lists potential hot water/boiler energy efficiency measures applicable to wineries in general. To determine the savings potential available at your winery, you need to
provide an indication of potential level of use of each of these measures in your winery considering the extent to which they have already been adopted. Do this by filling
in the column "potential application", below, as a percentage of possible applications for which you would like to use a given measure. Potential application here refers to
only fuels used for hot water generation. Entering 100% means all fuels used for hot water generation, not 100% of energy or fuel use.
#DIV/0!
Descriptions are accessed by scrolling your cursor over the cells in this column.
Share Boiler Fuel Use (of total fuel use): | 85% | #DIV/0! | kBtu/case
Measures | Potential Application | Typical Energy Savings |  | Typical Investments | Total Energy Savings |  | Total Costs | Payback Period | Notes
|  | % of Boiler Fuel |  |  | % of Boiler Fuel
| (%) |  | kBtu/case | $/MBtu-saved |  | MBtu/year | $ | years
Ozone Cleaning Barrels | 0% | 11% | #DIV/0! | 0 | 0% | #DIV/0! | 0 | 0
Improved Boiler Maintenance | 0% | 10% | #DIV/0! | 2.9 | 0% | #DIV/0! | #DIV/0! | #DIV/0!
Reduce Flue Gas Volume | 0% | 5% | #DIV/0! | 2.9 | 0% | #DIV/0! | #DIV/0! | #DIV/0!
Reduce Excess Inlet Air | 0% | 8% | #DIV/0! | 7.6 | 0% | #DIV/0! | #DIV/0! | #DIV/0!
Correct Sizing of Boiler | 0% | 8% | #DIV/0! | 11 | 0% | #DIV/0! | #DIV/0! | #DIV/0!
Improve Insulation of Boiler | 0% | 15% | #DIV/0! | 3.8 | 0% | #DIV/0! | #DIV/0! | #DIV/0!
Solar Water Heating | 0% | 40% | #DIV/0! | 30.4 | 0% | #DIV/0! | #DIV/0! | #DIV/0!
Return Condensate/Used Water | 0% | 10% | #DIV/0! | 4.2 | 0% | #DIV/0! | #DIV/0! | #DIV/0!
Relocate Boiler | 0% | 5% | #DIV/0! | 10 | 0% | #DIV/0! | #DIV/0! | #DIV/0!
Repair Leaks in Distribution Piping | 0% | 3% | #DIV/0! | 1.3 | 0% | #DIV/0! | #DIV/0! | #DIV/0!
Maintain Insulation Hot Water Piping | 0% | 5% | #DIV/0! | 1.9 | 0% | #DIV/0! | #DIV/0! | #DIV/0!
Insulate Hot Water Distribution Pipes | 0% | 7% | #DIV/0! | 3.8 | 0% | #DIV/0! | #DIV/0! | #DIV/0!
Heat exchanger replaces tank water heating | 0% | 6.21% | #DIV/0! | 107.14 | 0% | #DIV/0! | #DIV/0! | #DIV/0! | When other benefits are taken into account, payback is less than one year.
Total Potential Energy Savings | #DIV/0! | MBtu/year
Total Investments | #DIV/0! | $
Total Average Payback Period | #DIV/0! | years
Note on A17: Barrel cleaning consumes around 1.6 gallons of warm water per barrel. Moving to an ozone cleaning system (see water efficiency opportunities) eliminates the use of hot water for barrel cleaning. The degree of application is selected in the water efficiency sheet. The marginal costs are zero as the costs of the measure have already been accounted with water efficiency.
Note on A18: A simple maintenance program to ensure that all components of the boiler are operating at peak performance can result in substantial savings. In the absence of a good maintenance system, the burners and condensate return systems can wear or get out of adjustment. Fouling of the fireside of the boiler tubes or scaling on the waterside of the boiler should also be controlled. These factors can end up costing a steam system up to 20-30% of initial efficiency over 2-3 years (DOE, 2001a). We estimate a 10% possible energy savings on average (DOE, 2001a). Improved maintenance may also reduce the emission of criteria air pollutants. Numerous case studies estimate an average payback period for boiler maintenance of approximately 8 months.
Note on A19: Often excessive flue gas results from leaks in the boiler and the flue. This reduces the amount of heat transferred to the steam, and increases pumping requirements. These leaks are often easily repaired. Savings amount to 2-5% of the energy formerly used by the boiler (DOE, 2001b). The payback period is between 1 and 2 years. Flue gas monitors maintain optimum flame temperature and monitor carbon monoxide (CO), oxygen and smoke, by controlling the amount of inlet air. The oxygen content of the exhaust gas is a combination of excess air (which is deliberately introduced to improve safety or reduce emissions) and air infiltration (air leaking into the boiler). By combining an oxygen monitor with an intake airflow monitor, it is possible to detect even small leaks. A small 1% air infiltration will result in 20% higher oxygen readings. A higher CO or smoke content in the exhaust gas is a sign that there is insufficient air to complete the fuel burning. Using a combination of CO and oxygen readings, it is possible to optimize the fuel/air mixture for high flame temperature (and thus the best energy efficiency) and lower air pollutant emissions. We assume that this measure can be applied to large boilers only because small boilers will not make up the initial capital cost as easily.
Note on A20: The more air is used to burn the fuel, the more heat is wasted in heating this air rather than in producing steam. Air slightly in excess of the ideal stochiometric fuel/air ratio is required for safety, and to reduce NOx emissions, but approximately 15% is adequate (DOE, 2001a; Ganapathy, 1994). Poorly maintained boilers can have up to 140% excess air, but this is rare. Reducing this boiler back down to 15% even without continuous automatic monitoring would save 8% of total fuel use. The vast majority of boilers already operate at 15% excess air or lower, and thus this measure is not considered significant (Zeitz, 1997). However, if the boiler is using excess air, numerous case studies indicate an average payback period for this measure of 8 months. A rule of thumb often used is that boiler efficiency can be increased by 1% for each 15% reduction in excess air or 40°F (22°C) reduction in stack gas temperature (DOE, 2001a). CIPEC (2001a) estimates reducing oxygen (O2) in the flue gas by 1% increases boiler efficiency by 2.5%.
Note on A21: Correctly designing the boiler system at the proper steam pressure can save energy by reducing stack temperature, reducing piping radiation losses and reducing leaks in traps and other sources. In a study done in Canada on 30 boiler plants, savings from this measure ranged from 3% to 8% of the total gas consumption (Griffin, 2000). Savings were greatest when the pressure is reduced below 70 psig. If hot water demand varies widely over time, it may be beneficial to ‘cascade’ a number of smaller boilers. With increasing hot water demand, more boilers will run. The advantage is that the boilers will always run near its peak efficiency at full load. Cascading boiler systems, using multiple boilers sized for domestic applications, are used by commercial facilities in The Netherlands and Belgium These systems result in reduced purchase costs (due the purchase of a mass-produced boiler), reduced need for spare capacity, as well as reduced operation costs. These systems are only applicable to small wineries, and need to be properly designed and operated by a computerized energy management system. The energy savings for properly sizing of boilers is estimated at 8% of boiler fuel use. The payback period will depend strongly on the size and age of the existing boiler(s), as well as fuel prices. For calculation purposes we assume a payback period of 3 years. Only a detailed assessment of the specific boiler(s) will provide a more correct cost estimate.
Note on A22: It is possible to use new materials that insulate better, and have a lower heat capacity (and thus warm up faster). Savings of 6-26% can be achieved if this improved insulation is combined with improved heater circuit controls. Improved control is required to maintain the output temperature range of the old firebrick system. Because of the ceramic fiber’s lower heat capacity, the output temperature is more vulnerable to temperature fluctuations in the heating elements (Caffal, 1995). An additional benefit is that heating is more rapid when starting the boiler. Several case studies estimate an average payback period for this measure of about 1 year.
Note on A23: A solar boiler uses solar energy to (pre-) heat the water in a solar collector. Solar boilers have mainly been design for small-scale household applications or to heat pools. However, for small wineries a solar boiler may be a good alternative. The harvesting season sees a major part of the water use for cleaning (excluding year-round operation of a bottling facility), and this is also a time with large availability of sunlight. A solar boiler may reduce the costs of hot water supply by up to 40-80%, strongly depending on the current hot water supply. Electric water heating is typically the most expensive option, followed by propane-fired systems, while natural gas is typically the cheapest hot water supply option. Most wineries will use natural gas as fuel for the hot water supply, which will limit the profitability of installing a solar water heater. For those systems, we estimate a payback period of 8 years. For electric systems the payback period may be as low as 2-4 years. A solar hot water system needs to be optimized for the specific location and application. Only an onsite assessment can provide a better estimate of the savings and profitability. When considering a solar water heater, a specialized contractor should be hired to advise on the installation specifications.
Note on A24: Reusing the hot condensate in the boiler saves energy, reduces the need for treated boiler feed water and reclaims sensible heat savings. Usually fresh water must be treated to remove solids that might accumulate in the boiler, and returning condensate can substantially reduce the amount of purchased chemical required to accomplish this treatment. The fact that this measure can save substantial energy costs and purchased chemicals costs makes building a return piping system attractive. We assume a 10% energy savings and found an average payback period of about 1.1 years.
Note on A25: Transport of hot water will lead to energy losses in the piping. While energy losses can be reduced (see below) the location of the boiler near the major hot water uses (e.g. bottling line, malolactic fermentation tanks) would minimize the transport losses. Assuming a well-maintained hot water distribution network the savings by minimization of transport distance are estimated at 5%. The costs will strongly depend on the local conditions and layout of the winery. We assume a payback period of 3 years.
Note on A26: Distribution pipes themselves often have leaks that go unnoticed without a program of regular inspection and maintenance. In addition to saving 3% of energy costs, having such a program can reduce the likelihood of having to repair major leaks, thus saving even more in the long term (DOE, 2001a). Average payback period from several case studies is estimated at about 4 months.
Note on A27: It is often found that after heat distribution systems have undergone some form of repair, the insulation is not replaced. In addition, some types of insulation can become brittle or rot under normal wear. As a result, a regular inspection and maintenance system for insulation can save energy (Zeitz, 1997). Exact energy savings and payback periods are unknown and vary based on the existing practices.
Note on A28: Using more insulating material or using the best insulation material for the application can save energy in hot water and steam systems. Crucial factors in choosing insulating material include low thermal conductivity, dimensional stability under temperature change, resistance to water absorption and resistance to combustion. Other characteristics of insulating material may also be important depending on the application. These characteristics include tolerance of large temperature variation and system vibration and compressive strength where insulation is load bearing (Baen and Barth, 1994). Improving the insulation on the existing U.S. stock of heat distribution systems would save an average of 3-13% in all systems (DOE, 2001a). CIPEC (2001a) estimates that insulating a 10 foot long 4 inch steam pipe can be paid back in less than 6 months. For hot water systems we estimate the payback period at 1 year.
Note on A29: After wines are done fermenting, wines are generally heated to 50 to 54 degrees F for bottling (so that the labels stick). For wineries that do on-site bottling, using a heat exchanger in the pre-bottling area more efficiently warms the wine while reducing water consumption and lowering maintenance costs. Fetzer Vineyards installed a heat exchanger in its winery and found energy savings of 69%.
Note on B14: Fill in the share of total hot water energy to which you wish to apply the energy efficiency measure
Note on E14: Total typical investments, expressed as a function of annual energy savings

## EE-Other_fuels (hidden)
MISCELLANEOUS FUEL MEASURES
This Sheet lists general potential energy efficiency measures applicable to wineries in general. To determine the savings potential available at your winery, you need to
provide an indication of potential level of use of each of these measures in your winery considering the extent to which they have already been adopted. Do this by filling
in the column "potential application", below, as a percentage of possible applications for which you would like to use a given measure. Potential application here refers to
the fuel use specified in column B. Entering 100% means all of the listed fuel use on this sheet, not 100% of energy or fuel use.
#DIV/0!
Descriptions are accessed by scrolling your cursor over the cells in this column.
Measures - Fuels | Fuel Use to Which Measure Applies | Potential Application | Typical Energy Savings |  | Typical Investments | Total Energy Savings |  | Total Costs | Payback Period | Notes
|  | % of Total Fuel Use |  |  |  | % of Total Fuel Use | MBtu/yr
| (MBtu) |  | % | MBtu/case | $/MBtu saved |  |  | $ | years
Weekend setback temperatures | #DIV/0! | 0% | 100% | #DIV/0! | 1.05 | 0% | #DIV/0! | #DIV/0! | #DIV/0!
Total Potential Energy Savings |  | #DIV/0! | kWh/year
Total Investments |  | #DIV/0! | $
Total Average Payback Period |  | #DIV/0! | years
Note on A17: Setting building temperatures lower during the winter or higher during the summer over the weekend and during non-production times for appropriate buildings (e.g. office buildings during the weekend) can save energy by reducing heating or cooling needs. Hundreds of case studies in the IAC database (2001) estimate costs to be very small. Averaging the IAC case studies shows typical investment per MBtu saved to be just over $1.
Note on B14: This energy use can be changed by user or default values can be used.
Note on F14: Total typical investments, expressed as a function of annual energy savings

## EE-Other_electric (hidden)
MISCELLANEOUS ELECTRICITY MEASURES
This Sheet lists general potential energy efficiency measures for electricity applicable to wineries in general. To determine the savings potential available at your winery, you
need to provide an indication of potential level of use of each of these measures in your winery considering the extent to which they have already been adopted. Do this by
filling in the column "potential application", below, as a percentage of possible applications for which you would like to use a given measure. Potential application here refers to
the electricity use specified in column B. Entering 100% means 100% of the listed electricity use on this sheet, not 100% of energy or electricity use. The last measure,
photovoltaics, unlike the other previous measures, requires you to fill in the applicable kWh, instead of potential application.
Only fill in the yellow cells. Other cells contain default values, or are calculated.
#DIV/0!
Descriptions are accessed by scrolling your cursor over the cells in this column.
Measures - Electricity | Energy Use to which Measure Applies | Potential Application | Typical Energy Savings |  | Typical Investments | Total Energy Savings |  | Total Costs | Payback Period | Notes
|  |  | % of Total Electricity |  |  | % of Total Electricity
| (kWh) | (%) |  | kWh/case | $/kWh-saved |  | kWh/yr | $ | years
Energy Management Systems | 0 | 0% | 3% | #DIV/0! | 0.13 | 0% | 0 | 0 | #DIV/0!
Efficient Transformers | 0 | 0% | 30% | #DIV/0! | 0.14 | 0% | 0 | 0 | #DIV/0!
Power Factor Correction Systems | 0 | 0% | 2% | #DIV/0! | 0.22 | 0% | 0 | 0 | #DIV/0!
Power Management Office Equipment | #DIV/0! | 0% | 50% | #DIV/0! | 0.05 | 0% | #DIV/0! | #DIV/0! | #DIV/0!
Electronic controls to turn off equipment | #DIV/0! | 0% | 30% | #DIV/0! | 0.03 | 0% | #DIV/0! | #DIV/0! | #DIV/0!
Anaerobic Digestion | #DIV/0! | 0% | 24% | #DIV/0! | 0.7 | 0% | #DIV/0! | #DIV/0! | #DIV/0!
Photovoltaics | 0 | #DIV/0! | 100% | #DIV/0! | 3.85 | #DIV/0! | 0 | 0 | #DIV/0!
Total Potential Energy Savings |  | #DIV/0! | kWh/year
Total Investments |  | #DIV/0! | $
Total Average Payback Period |  | #DIV/0! | years
Note on A18: Changing how energy is managed by implementing an organization-wide energy management program is one of the most successful and cost-effective ways to bring about energy efficiency improvements. An energy management program creates a foundation for positive change and provides guidance for managing energy throughout an organization. In companies without a clear program in place, opportunities for improvement may be known but may not be promoted or implemented because of organizational barriers. A successful program in energy management begins with a strong commitment to continuous improvement of energy efficiency. This involves assigning oversight and management duties to an energy director, establishing an energy policy, and creating a cross-functional energy team. Steps and procedures are then put in place to assess performance, through regular reviews of energy data, technical assessments and benchmarking. From this assessment, an organization is able to develop a baseline of energy use and set goals for improvement. Performance goals help to shape the development and implementation of an action plan. An important aspect for ensuring the successes of the action plan is involving personnel throughout the organization. Personnel at all levels should be aware of energy use and goals for efficiency. Staff should be trained in both skills and general approaches to energy efficiency in day-to-day practices. In addition, performance results should be regularly evaluated and communicated to all personnel, recognizing high achievement. Evaluating performance involves the regular review of both energy use data and the activities carried out as part of the action plan. Information gathered during the formal review process helps in setting new performance goals and action plans and in revealing best practices. Establishing a strong communications program and seeking recognition for accomplishments are also critical steps. Strong communication and receiving recognition help to build support and momentum for future activities. The potential savings achieved through an energy management system vary widely. Conservatively, we assume that winery-wide savings of 3% are possible through increased attention (besides the potential savings from specific measures described elsewhere).
Note on A19: Wineries may have various transformers onsite to produce low voltage. Transformers may have losses equivalent up to 3%. By replacing the transformers by more energy efficient models, energy losses can be reduced by roughly 30% (depending on the typical load of the specific transformer). The ENERGY STAR program has labeled various efficient transformer models (see also www.energystar.gov). The ENERGY STAR transformers demonstrate lower losses at various load levels. The payback period based on the marginal costs of installing an efficient transformer is generally less than 1-2 years (Fetters, 2002).
Note on A20: Computers, variable speed drives, welding arcs and other equipment can lead to poor power quality. The distortion of the harmonics can lead to an increased energy bill and reduced efficiency (through increased generation of heat) while heavily distorted harmonics may damage equipment. The losses may vary widely from one site to another, depending on the electricity end uses and maintenance of the equipment. We assume that on average the losses are in the order of 2-3%. Installing power factor management (or filters) may reduce these losses. The payback period of installing harmonic filters depends on the capacity, and may vary between 12 and 18 months. We conservatively assume a payback period of 18 months. Alternatively, when purchasing equipment, compliance with IEEE Standard 519 is important (see http://www.ieee.org/portal/site for more information).
Note on A21: Office equipment (e.g. computers, copiers), while small in a winery, are often left on overnight or during periods that they are not used. ENERGY STAR office equipment has power management software to turn off (or down) equipment after a set period of time. However, often this is not properly installed. Surveys of after-hours use of equipment has found that generally 50% of the computers in small businesses is not turned off or down (Roberson et al, 2004). A monitor turned down uses only 10% of the energy of a monitor without power management options installed. Properly installing the software or controls may lead to savings of 50% or more (assuming 10 hours of use/day, and going to sleep mode). Furthermore, turning equipment off manually may lead to additional savings (up to 10%). This has been covered by the measure Energy Management Systems.
Note on A22: Electronic controls can be as simple as on/off switches to be switched off during non-operating hours. According to the IAC database (2001), implementation costs range from $150 for simple controls to almost $3000 for industry specific controls on industrial equipment and HVAC. We assume an average cost of implementation from all of the case studies in the IAC database affecting electricity use, likely a conservative estimate for simple HVAC controls. We assume this measure will apply to miscellaneous equipment as well as offices and HVAC.
Note on A23: Generally, winery wastewater is aerobically treated in ponds, using a considerable amount of electricity for aeration. After many years of research and experimentation worldwide, technologies have been developed that allow anaerobic digestion of winery wastes. Various wineries in France, South Africa, Australia and the U.S. use the technology to treat wastewater. In the U.S., the Canandaigua Winery (New York) has installed the first anaerobic digestion system in 1997, and since then expanded the system. The system reduced electricity consumption for wastewater treatment by approximately 7,160 kWh/day, or 68% compared to the previously used aerobic pond system. The biogas generated in the digester is used to heat the digester. Excess gas could be used for power generation. Furthermore, the system resulted in reduced costs for sludge disposal, due to the reduced sludge volume (Quinn, 2002). This has resulted in a cost reduction for wastewater treatment of $0.03/case. Investment costs for an anaerobic digestion system are relatively high, but the benefits may warrant the investments. Typically, the payback period of anaerobic digesters in agriculture is between 3 and 7 years (AgStar, 2004). The investments for the Canandaigua Winery were not available, as the project was financed by the technology provider (now called Ecovation, Inc.).
Note on A24: Photovoltaic (PV) cells directly generate electricity from solar light. Although the technology is still expensive (but coming down in price continuously), PV generates power during the peak of demand (e.g. during the crush, and the middle of the day). This reduces peak demand and may offset high power rates. Furthermore, PV systems do not generate any emissions, last for 20 years or longer, have no movable parts, and require little maintenance. PV systems are generally installed as rooftop systems, so that they do not use any additional space. A number of wineries (e.g. Fetzer Vineyards (41 kW), Ridge Vineyards (65 kW), St. Francis (457 kW), Rodney Strong (766 kW), Domaine Carneros (120 kW), and Mount Eden (20 kW)) have installed PV-systems. The PV systems not only reduce electricity demand, they contribute to sustainable development of the winery and a positive public image. Various suppliers in California can supply and install PV systems (e.g. Powerlight, Akeena, Premier Power, Renewable Technologies, Inc.). PG&E and other utilities provide rebates for installing PV systems, while California regulation allows net metering of PV-generated electricity (i.e. power generated from a PV system can be fed to the grid against the full purchase price of the electricity).
Note on B15: The amount of energy use to which the measure applies is estimated on the basis of the model winery. Values can be changed by the user.
Note on B24: Enter the power generated by the PV system annually.
Note on C15: Fill in the share of the applications to which the measure can still be implemented
Note on C18: % of electricity use that will be controlled through improved management practices
Note on C21: % of office equipment to which power management software can be properly installed
Note on F15: Total typical investments, expressed as a function of annual energy savings
Note on F24: Typical investments without rebates. When rebates are available, deduct the amount of the rebates as share of the typical costs.

## EE-CHP (hidden)
COGENERATION (also called Combined Heat and Power, or CHP)
This Sheet lists potential types of cogeneration measures applicable to wineries in general. To determine the savings potential available at your winery, you need to
provide an indication of potential level of use of each of these measures in your winery considering the extent to which they have already been adopted. Do this by
filling in the column "potential application", below, as a percentage of possible applications for which you would like to use a given measure. Potential application here
refers to the share of electricity use. Entering 100% here does 100% of electricity use. Therefore, cumulative application cannot exceed 100%.
If you want to change the default assumptions for cogeneration or trigeneration, please use the Module Calculation for Cogeneration below.
#DIV/0!
Descriptions are accessed by scrolling your cursor over the cells in this column.
Measures | Potential Application | Typical Energy Savings |  | Typical Investments | Total Electricity Savings |  | Additional Fuel Use | Total Costs | Payback Period | Notes
% of Total Electricity
| (%) | kWh/case |  | $/kWh-saved |  | kWh/year | MBtu/year | $ | years
Cogeneration - Engine | 0% | 0.13628 |  | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0!
Cogeneration - Microturbine | 0% | 0.099941 |  | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0!
Trigeneration - Engine | 0% | 1.0632 |  | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0!
Trigeneration - Microturbine | 0% | 0.80534 |  | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0!
Total Potential Energy Savings | 0 | kWh/year
Total Additional Natural Gas Use | 0 | MBtu/year
Total Investments | #DIV/0! | $
Total Average Payback Period | N/A | years
Calculation for Cogeneration and Trigeneration
Cogeneration (power and heat) - Sized to Heat Demand
System | Engine | Microturbine
Power to Heat Ratio | 0.75 | 0.55
Heat Rate (Btu/kWh) | 10500 | 13544
Specific heat production (Btu/case) | 620 | 620
Specific power production (kWh/case) | 0.13628 | 0.099941
Specific power savings (kWh/case) | 0.13628 | 0.099941
Total Power Savings (kWh/year) | 0 | 0
Additional Natural Gas Use (MBtu/year) | 0 | 0
Additional Natural Gas Use ($/year) | #DIV/0! | #DIV/0!
Installed Capacity (kW) | 0 | 0
Capital Costs ($) | 0 | 0
Rebate ($) | 0 | 0
Maintenance costs ($/year) | 0 |  | 0
Energy Cost Savings ($) | #DIV/0! | #DIV/0!
Payback Period (years) | #DIV/0! | #DIV/0!
Trigeneration (power, cooling and heat) - Sized to Power Demand
System | Engine | Microturbine
Power to Heat Ratio | 0.75 | 0.55
Heat Rate (Btu/kWh) | 10500 | 13544
Specific heat production (Btu/case) | 4400 | 4400
Specific power production (kWh/case) | 0.96717 | 0.70926 | 0
Provided Cooling Power-Equi. (kWh/case) | 0.096074 | 0.096074 | -0.1241
Specific power savings (kWh/case) | 1.0632 | 0.80534 | -0.1241
Total Power Savings (kWh/year) | 0 | 0
Additional Natural Gas Use (MBtu/year) | 0 | 0
Additional Natural Gas Use ($/year) | #DIV/0! | #DIV/0!
Installed Capacity (kW) | 0 | 0
Capital Costs ($) | #DIV/0! | #DIV/0! | 0
Rebate ($) | 0 | 0 | 0
Maintenance costs ($/year) | #DIV/0! | #DIV/0!
Energy Cost Savings ($) | #DIV/0! | #DIV/0! | #DIV/0!
Payback Period (years) | #DIV/0! | #DIV/0!
Default Assumptions
COP Adsorption Chiller | 0.7
COP Conventional Chiller (fermentation) | 4.1
Investment Costs ($/kW) | 1160 | 1926
Investment Costs ($/kW, incl. adsorption) | #DIV/0! | #DIV/0!
Maintenance Costs ($/kWh) | 0.014 | 0.015
Maintenance Costs ($/kWh, incl. adsorption) | #DIV/0! | #DIV/0!
Average Running Time (Hours/year) | 4380 | 4380
Note on A15: Cogeneration is the combined production of heat and power (electricity) (CHP). The heat can also be used to drive an absorption or adsorption chiller, generating power, heat and cold. This is also called tri-generation. (See Trigeneration measures, below). The central part of the cogeneration unit is called the prime mover. The prime mover is used to generate power. The waste heat of the prime mover is used to produce hot water, steam or direct heat. Given the size of most wineries, there are basically two types of prime movers: reciprocating engines or microturbines. Reciprocating gas engines are the more traditional prime mover. They are sold in sizes of 100 kWe to 15 MWe. They use the same technique as diesel backup generators, but burn natural gas instead. Engines offer low first-cost, fast start-up, proven reliability when properly maintained, excellent load-following characteristics and significant heat recovery potential (Goldstein et al., 2003). The technology has improved over the past decades to increase fuel efficiency, reduce emissions and improved maintenance. The heat rate for reciprocating engines varies between 10,000 to 10,970 Btu/kWh (HHV) and electric efficiencies varying between 28 and 40% (LHV). Waste heat is recovered as hot water from the exhaust and cooling water of the engine. The power to heat ratio for engine-based CHP systems varies between 0.5 and 1 (i.e. for every unit of power, 1 tot 2 units of heat are produced). The investment costs of a reciprocating engine-based CHP system are estimated at $900-1500/kWe and maintenance costs vary between $0.007 and $0.02 per kWh produced (Oland, 2004). Many manufacturers supply engines (e.g. Caterpillar, Perkins, Waukesha
Note on A16: Cogeneration is the combined production of heat and power (electricity) (CHP). The heat can also be used to drive an absorption or adsorption chiller, generating power, heat and cold. This is also called tri-generation (see Trigeneration measures, below). The central part of the cogeneration unit is called the prime mover. The prime mover is used to generate power. The waste heat of the prime mover is used to produce hot water, steam or direct heat. Given the size of most wineries, there are basically two types of prime movers: reciprocating engines or microturbines. Microturbines are a new opportunity for small-scale cogeneration units. They are turbines that burn natural gas that range from 30 kWe to 400 kWe electric output. The efficiency of the current generation of microturbines is slightly lower than that of reciprocating engines. Because microturbines have fewer moving parts, they have the potential for lower maintenance costs, simplified installation and increased reliability (Goldstein et al., 2003). Microturbines have also lower emissions compared to engines. The heat rate of microturbines varies between 13,000 and 15,000 Btu/kWh and electric efficiencies varying between 25 and 29% (LHV). Waste heat is generated as low-pressure steam or hot water. The power to heat ratio of microturbine-based systems varies between 0.4 and 0.7 (i.e. for each unit of power, 1.4 to 2.5 units of heat are generated). The investments of a microturbine-based CHP system are estimated at $1700-2600/kWe, while maintenance costs are lower than $0.018/kWh (Oland, 2004). Vineyard 29 in Napa has installed two microturbines as part of a tri-generation plant. Important suppliers of microturbines are Capstone and Solar Turbines.
Note on A17: A cogeneration system should be optimized based on the demand for cooling and heating. A careful analysis of energy consumption data for a number of years is necessary to scale the system to the needs of the site. Generally, the system will be designed to meet the baseload, while peak demand during the crush (for fermentation) will be met with additional cooling equipment. Adsorption/absorption cooling is a technology to use the recovered heat from the cogeneration unit to provide cooling. The cooling can be used for fermentation tanks, and for other parts of the winery depending on demand. Absorption cooling is used in many applications. The absorption cooling principle is based on the fact that ammonia is extremely soluble in cold water and much less in hot water. Thus, if a water ammonia solution is heated, it expels its ammonia. After dissipating the heat, the ammonia gas – still under high pressure – liquefies. The liquid ammonia flows into a section of the machine, where it comes in contact with hydrogen gas, which absorbs ammonia gas with a cooling effect. The hydrogen-ammonia mixture then meets a surface of cold water, which absorbs the ammonia again, closing the cycle. Absorption coolers are produced by a number of suppliers (e.g. Carrier, York, Trane, Robur, McQuay, LG Machinery, and Century). Absorption coolers can be found in different wineries and at varying scales. E. and J. Gallo uses a 500 ton absorption chiller at it’s Modesto facility for the cooling of stored wine. In contrast, adsorption cooling utilizes the capacity of certain substances to adsorb water on their surface, from where it can be separated again with the application of heat. Adsorption units use hot water from the cogeneration unit. These systems do not use ammonia or corrosive salts, but use silica gel, reducing maintenance. Adsorption units were originally developed in Japan (by e.g. Mycom and Nishiyodo Kuchou) and are now also marketed in the U.S. (by HIJC USA, Houston, TX). Four industrial sites in California use this technology (see also below), while it has a proven track record in Japan and selected sites in Europe. The thermal performance of both systems is similar with a COP (coefficient of performance) between 0.68 and 0.75, and capital costs are comparable. However, the reliability of an adsorption unit is expected to be better, and maintenance cost is expected to be lower. In 2003, Vineyard 29 in Napa installed two 120 kW microturbines (Capstone C60) to supply power to the winery, hot water and cooling. The cooling is provided by an adsorption unit using the hot water generated by the micro turbines. The system is sized to meet the baseload heating and cooling needs. Extra cooling needed during fermentation is provided by a traditional cooling system. The system allows a reduction of electricity demand during the summer peak, reducing the electricity rates for the winery. Vineyard 29 received financial support for the cogeneration system from the utilities. The investments are around $400,000. A rebate of $200,000 reduced the payback period of the system to an estimated at 2-3 years (Coggan, 2004).
Note on A18: A cogeneration system should be optimized based on the demand for cooling and heating. A careful analysis of energy consumption data for a number of years is necessary to scale the system to the needs of the site. Generally, the system will be designed to meet the baseload, while peak demand during the crush (for fermentation) will be met with additional cooling equipment. Adsorption/absorption cooling is a technology to use the recovered heat from the cogeneration unit to provide cooling. The cooling can be used for fermentation tanks, and for other parts of the winery depending on demand. Absorption cooling is used in many applications. The absorption cooling principle is based on the fact that ammonia is extremely soluble in cold water and much less in hot water. Thus, if a water ammonia solution is heated, it expels its ammonia. After dissipating the heat, the ammonia gas – still under high pressure – liquefies. The liquid ammonia flows into a section of the machine, where it comes in contact with hydrogen gas, which absorbs ammonia gas with a cooling effect. The hydrogen-ammonia mixture then meets a surface of cold water, which absorbs the ammonia again, closing the cycle. Absorption coolers are produced by a number of suppliers (e.g. Carrier, York, Trane, Robur, McQuay, LG Machinery, and Century). Absorption coolers can be found in different wineries and at varying scales. E. and J. Gallo uses a 500 ton absorption chiller at it’s Modesto facility for the cooling of stored wine. In contrast, adsorption cooling utilizes the capacity of certain substances to adsorb water on their surface, from where it can be separated again with the application of heat. Adsorption units use hot water from the cogeneration unit. These systems do not use ammonia or corrosive salts, but use silica gel, reducing maintenance. Adsorption units were originally developed in Japan (by e.g. Mycom and Nishiyodo Kuchou) and are now also marketed in the U.S. (by HIJC USA, Houston, TX). Four industrial sites in California use this technology (see also below), while it has a proven track record in Japan and selected sites in Europe. The thermal performance of both systems is similar with a COP (coefficient of performance) between 0.68 and 0.75, and capital costs are comparable. However, the reliability of an adsorption unit is expected to be better, and maintenance cost is expected to be lower. In 2003, Vineyard 29 in Napa installed two 120 kW microturbines (Capstone C60) to supply power to the winery, hot water and cooling. The cooling is provided by an adsorption unit using the hot water generated by the micro turbines. The system is sized to meet the baseload heating and cooling needs. Extra cooling needed during fermentation is provided by a traditional cooling system. The system allows a reduction of electricity demand during the summer peak, reducing the electricity rates for the winery. Vineyard 29 received financial support for the cogeneration system from the utilities. The investments are around $400,000. A rebate of $200,000 reduced the payback period of the system to an estimated at 2-3 years (Coggan, 2004).
Note on B12: Fill in the share of total CHP energy (see inventory below) to which you wish to apply the energy efficiency measure
Note on B31: Can vary between 0.5 and 1, depending on type of engine
Note on B32: Varies between 10,035 and 10,967 Btu/kWh, depending on specific engine
Note on B41: Rebates may apply to cogeneration systems. Fill in the size of the rebate (if known)
Note on B49: Can vary between 0.5 and 1, depending on type of engine
Note on B50: Varies between 10,035 and 10,967 Btu/kWh, depending on specific engine
Note on B60: Rebates may apply to cogeneration systems. Fill in the size of the rebate (if known)
Note on B69: Varies between 900 and 1500 $/kWe
Note on B71: Varies between 0.007 and 0.02 $/kWh
Note on C31: Can vary between 0.5 and 1, depending on specific system
Note on C32: Varies between 13,100 and 15,000 Btu/kWh, based on specific turbine
Note on C41: Rebates may apply to cogeneration systems. Fill in the size of the rebate (if known)
Note on C49: Can vary between 0.5 and 1, depending on specific system
Note on C50: Varies between 13,100 and 15,000 Btu/kWh, based on specific turbine
Note on C60: Rebates may apply to cogeneration systems. Fill in the size of the rebate (if known)
Note on E12: Total typical investments, expressed as a function of annual energy savings

## WE-Water (hidden)
WATER EFFICIENCY IMPROVEMENT OPPORTUNITIES
This Sheet lists potential water efficiency measures applicable to wineries in general. To determine the savings potential available at your winery, you need to provide
an indication of potential level of use of each of these measures in your winery considering the extent to which they have already been adopted. Do this by filling in the
column "potential application", below, as a percentage of possible applications within the specific area of water use. Potential application here refers to only water used
in the applicable area of the winery, as listed in the first column (general water measures refers to all water, whereas barrel cleaning refers on to water used in cleaning
barrels). Entering 100% means that you would like to adopt the measure wherever possible in your winery. For example, 100% of ozone tank
cleaning applies to all tank cleaning water. | #DIV/0!
Descriptions are accessed by scrolling your cursor over the cells in this column.
Water Use |  | #DIV/0! | Gallon/case produced
|  | #DIV/0! | Gallon/case bottled
Measures | Potential Application | Typical Water Savings |  | Typical Investments | Total Water Savings |  | Total Costs | Payback Period | Notes
|  | % of Total Water |  |  | % of Total Water
| (%) |  | Gallon/case | $/Gallon-saved |  | Gallon/year | $ | years
General Water Measures
Water Management Program | 0% | 5% | #DIV/0! | 0.00047488 | 0% | #DIV/0! | #DIV/0! | #DIV/0! | Capital costs are small and include personnel awareness and metering.
Repair Leaks | 0% | 2% | #DIV/0! | 0 | 0% | #DIV/0! | #DIV/0! | #DIV/0! | Typical investments per gallon saved is generally insignificant.
General Cleaning
Sweeping floors before water washing | 0% | #DIV/0! | #DIV/0! | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Costs are negligible per gallon saved.
High Pressure nozzles with automatic shutoff devices | 0% | #DIV/0! | #DIV/0! | 0.00033534 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
Barrel Cleaning
High pressure nozzle - tank cleaning | 0% | #DIV/0! | #DIV/0! | 0.01224 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
Ozone tank cleaning of barrels | 0% | 11% | #DIV/0! | 0.0076058 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
Automatic cleaning systems | 0% | #DIV/0! | #DIV/0! | 0.022 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
Cooling Tower
Alternative sources of make-up water | 0% | #DIV/0! | #DIV/0! | 0.0014 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
Replace single pass cooling system with cooling tower | 0% | #DIV/0! | #DIV/0! | 0.002619 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
Reduce bleed off in cooling tower | 0% | #DIV/0! | #DIV/0! | 0.0026 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
Operate bleed off continuously/install controls | 0% | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
Evaporative Cooling
Replace non-recirculating evaporative coolers | 0% | #DIV/0! | #DIV/0! | 0.0022941 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
Reuse bleed-off water in evaporative cooling | 0% | #DIV/0! | #DIV/0! | 0.0026 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
Hot Water
Reduction of make-up water by reduction in energy use | 0% | #DIV/0! | #DIV/0! | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Calculations linked to EE-Hot Water sheet; if nothing is selected on EE-Hot
Return Condensate/Used Water | 0% | #DIV/0! | #DIV/0! | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Water sheet, savings will be 0.
Humidifiers
Controls and water supply valves | 0% | #DIV/0! | #DIV/0! | 0.07 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
Efficient humidifier models | 0% | #DIV/0! | #DIV/0! | 0.077 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
Caves for barrel storage | 0% | #DIV/0! | 0.07 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
Miscellaneous
Efficient toilets and building appliances | 0% | #DIV/0! | #DIV/0! | 0.005 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
Total Potential Water Savings | #DIV/0! | Gallons/year
Total Investments | #DIV/0! | $
Total Average Payback Period | #DIV/0! | years
Note on A20: Like energy efficiency, we expect changing how water is managed by implementing an organization-wide water management program to be one of the most successful and cost-effective ways to bring about water efficiency improvements. A water management program creates a foundation for positive change and provides guidance for managing water throughout an organization. In companies without a clear program in place, opportunities for improvement may be known but may not be promoted or implemented because of organizational barriers. A successful program will have a water managing director and/or a water efficiency team, promoting water efficiency within the winery. Water should be metered and performance monitored. Performance should be assessed regularly through reviews of the data, technical assessments and benchmarking. Performance goals should also be set. Personnel throughout the winery should be aware of water use and goals for efficiency. North Carolina's Department of Environment and Natural Resources Division of Pollution Prevention and Environmental Assistance (2004) outlines 6 steps to a successful water efficiency program: 1. Establish commitment and goals 2. Line up support and resources 3. Conduct a water audit 4. Identify water management options 5. Prepare a plan and implement schedule 6. Track results and publicize success. According to California Sustainable Winegrowing Alliance, of wineries that have implemented a comprehensive water conservation program, monitored and recorded total use, set yearly goals and set up a water team, about 1/3 found savings of 15% and 2/3 found savings of 10% (CSWA, 2004). We conservatively assume a 5% savings for any winery that sets up a water conservation program, assuming most wineries have implemented some conservation measures already and not all savings will be realized immediately.
Note on A21: Facilities require ongoing leak detection and repairs if they are to maintain water efficiency. Leak detection should include all water uses and connections, including meters, water distribution lines, piping and connections for fixtures, appliances, process water, cooling water, hot water and landscaping. We assume repairing leaks applies to all water used, and do not split up this measure among the different processes. We leave this up to the user in the application potential box (column B). A variety of leak detection equipment is available, including leak detection services, water test flow kits (about $600-$1100) and portable metering devices (about $700-$1100). Generally, the costs per gallon saved are negligible.
Note on A23: Sweeping floors of large solid debris before washing with water will save water. We estimate a 20% savings of water used for washing floors in the crush pad, barrel room and bottling facilities. We assume 10% of the water used in those areas is for cleaning surfaces that could be swept. Costs are negligible (brooms, potentially slightly longer labor hours) compared to the cost of the gallons of water saved for this measure.
Note on A24: Installing high pressure nozzles with automatic shutoff devices can reduce water use by limiting water use from the hoses used for cleaning. According to Vickers (2001), these nozzles cost between $10 to $25 per nozzle, and savings can be as much as 40%. We assume savings of 40% that applies to 80% of the water used in the winery, crush pad, and storage areas, 10% of the water used in the barrel rooms, and 10% of the water used in bottling.
Note on A26: High pressure nozzles can provide more precise cleaning in a shorter time, using less water in the process. One model by Gamajet uses as little as 8 GPM for 1.5 minutes, cleaning a whole barrel with just 12 gallons of water. Compare this with a typical sprayball which uses 25 gallons per barrel. We estimate savings to be about 40% of all water used in barrel cleaning. We estimate about 80% of the water used in the barrel room is used to wash barrels, and 10% is used for floors and other cleaning (and 10% is for humidifiers). Gamajet costs $2,200 for their high pressure barrel washers. Multiple high pressure nozzles will be needed for wineries with more than one nozzle per tank cleaning line.
Note on A27: Ozone cleaning can eliminate the need for hot water use for barrel cleaning, reducing water use by 50%. We estimate typical water use for barrel cleaning at 1.6 gallon/case. Various suppliers provide (mobile) ozone generators. Ozone is a toxic gas. It is made onsite and on demand by a generator. This eliminates the risks of storage. Personnel using the ozone cleaning process should be properly trained. Typical costs: investments/operation
Note on A28: Automatic cleaning systems can combine high pressure and hot water in an automated system, reducing water use by as much as 80% compared to un-automated spray balls. Gamajet sells automated systems beginning at $9650. Other systems are produced by Tom Beard and Process Engineers and sell for about $26,000 to 27,000. We assume a typical two-barrel system will cost about $20,000 and will save 50% of water used in barrel washing.
Note on A30: Wineries that can reuse water from another process should consider using it in cooling make-up water. Water that is treated on site might be suitable for make-up water, though water softening treatment may be necessary to avoid phosphate scale buildup. One large project in the Netherlands set up a system amongst 9 companies, reusing process water for cooling water (European Environmental Press, 2000). They found costs of about 0.0015 Euros (or 0.0014 2000 US $) per gallon saved with a payback of about 4 months. These costs are an estimate as actual costs will vary depending on how much additional treatment is required, if any, and what kind of piping is needed to supply the cooling water.
Note on A31: As the name implies, once-through cooling systems use water once and dispose of it. Conversely, cooling towers recycle water within the tower, saving 90 to 95% of the water used in single pass systems. A hospital replaced their single pass systems with cooling towers for $5,500 and found savings of 2.1 million gallons per year. Similarly, an ink manufacturer replaced it's single pass system and found 80% savings. We used these studies to estimate costs of water saved, and estimated savings to be 90% of all cooling water used in single pass systems (Vickers, 2001).
Note on A32: By allowing higher concentrations of suspended and dissolved solids in the circulating water, bleed-off in the cooling tower is reduced, saving water. Of course, required quality regulations must be maintained. Adjusting the physical or chemical treatment of circulating water increases the cycles of concentration. The goal is to achieve the maximum number of cycles without forming scales. A reasonable goal in most cases is to achieve at least six cycles of concentration. Typical concentration ratios are two to three (North Carolina Department of Environment and Natural Resources Division of Pollution Prevention and Environmental Assistance, 2004). We conservatively assume most wineries that have not implemented this measure will begin at a concentration cycle of three. Typical savings achieved by increasing concentration cycles from 3 to 6 are about 20%. (Savings achieved by increasing cycles from 2 to 6 are 40%). The Ventura Coastal Plant which processes citrus fruit increased the concentration ratio of its cooling towers and evaporative coolers to 5, reducing bleed-off by 50% and saving almost 5,200 gallons per day (Department of Water Resources, California, 2004) with capital costs of $5,000, the payback period is about 7 months.
Note on A33: Cooling towers are usually bled off automatically in batches when the mineral concentration or conductivity reaches a certain level (Vickers, 2001). The batch method can result in wide fluctuations in bleed-off volumes without proper controls. Operating the cooling tower on a continuous basis to maintain conductivity can minimize water use during bleed-off. According to North Carolina's Department of Environment and Natural Resources Division of Pollution Prevention and Environmental Assistance, installing controls can help achieve optimal bleed-off. Submeters can be installed on most cooling towers for less than $1000. We assume a 5% reduction in cooling water requirements by implementing this measure.
Note on A35: Similar to cooling towers, once-through evaporative coolers use water only once and dispose of it. Conversely, recirculating evaporative coolers recycle water saving 70% of the water used in single pass evaporative coolers. Air cooled units save even more water. A hospital installed a recirculating cooling water system and found savings of 8.5 million gallons per year. Purchase and installation costs were $19,500 and savings totaled $55,685 per year, yielding a 4-month payback (Vickers, 2001). We used this study to estimate costs of water saved, and estimate savings to be about 70% of all cooling water used in once-through systems.
Note on A36: Like the cooling tower, bleed-off water in evaporative cooling should be minimized while maintaining discharge standards. We assume costs and savings similar to those for the cooling tower.
Note on A38: Reducing the overall hot water requirements in the boiler not only saves energy but also reduces the need for treated boiler feed water. Usually fresh water must be treated to remove solids that might accumulate in the boiler, so this measure can substantially reduce the amount of purchased chemicals required to accomplish this treatment, as well as the amount of water needed. The fact that this measure can save substantial energy costs, water costs and purchased chemicals costs makes reducing make-up water a particularly attractive measure. The degree of application is coupled to the measures on the energy efficiency sheet EE-hot water, hot water measures for energy efficiency. The marginal costs for reduction of water use is assumed to be zero, as all costs are assigned to hot water energy efficiency measures. The amount of water savings is also linked the amount of energy saved, already calculated on the EE-hot water sheet.
Note on A39: Boiler - return condensate. Reusing the hot condensate in the boiler saves energy, reduces the need for treated boiler feed water and reclaims sensible heat savings. Usually fresh water must be treated to remove solids that might accumulate in the boiler, and returning condensate can substantially reduce the amount of purchased chemical required to accomplish this treatment, as well as the amount of water needed. The fact that this measure can save substantial energy costs, water costs and purchased chemicals costs makes building a return piping system attractive. The degree of application is coupled to the return condensate measure in the sheet on EE-hot water, hot water measures for energy efficiency. The marginal costs for reduction of water use is assumed to be zero, as all costs are assigned to hot water energy efficiency measures. We assume a 20% savings of hot water is possible by returning condensate.
Note on A41: We assume a 10% savings in water due to controls and water supply valves. We also assume about 10% of the water used in the barrel rooms is used for humidification. TrueFog, USA manufactures complete control systems for $3290.
Note on A42: Low flow but better dispersive models can save water in humidification. We assume 10% of the water used in the barrel room is used for humidifiers, and that 50% of this can be saved by installing more efficient humidifier models. Efficient humidifier models should include adjustable water supply valves to control water flow.
Note on A43: The typical loss due to evaporation from the barrel in Northern California is around 4 gallons per barrel/year (Lewis and Leech, 2004). Caves maintain a constant humidity of 70-90%, and hence reduce the need for humidification for barrel storage. The degree of application is coupled to the area for which a cave is constructed as defined in the section on refrigeration measures. The marginal costs for reduction of water use is assumed to be zero, as all costs are assigned to refrigeration.
Note on A45: Standard toilets use 3.5 gpf. Water efficient (low-flow) designs use only 1.6 gpf. Studies have shown that water use is reduced by 19% on average due to low-flow toilets (http://www.epa.gov/owm/water-efficiency/toilets.htm). Experiences in various cities have demonstrated of these measures of about 1 year. We assume similar characteristics for other water efficiency measures, not used directly in the production process.
Note on B16: Fill in the share of total water to which you wish to apply the water efficiency measure.
Note on D18: Gallons per case produced unless otherwise stated
Note on D27: Gallons per case bottled
Note on D43: Gallons per case bottled
Note on E16: Total typical investments, expressed as a function of annual energy savings

## ASSESSMENT RESULTS (hidden)
SELF-ASSESSMENT RESULTS
The results of benchmarking your facility to a "reference" best practice winery producing the same products under similar conditions are presented below. The results of the analysis are expressed as an intensity index. The performance (or index) of the "reference" facility is 100. The higher the intensity index the larger the potential for efficiency improvement.
The results of the self-assessment are given in red. The results are given for the sum of all selected energy and water efficiency measures, as well as the average payback period.
| Energy Intensity Index (EII) | #NAME?
| EII (after implementation) | #DIV/0!
| Water Intensity Index (WII) | #NAME?
| WII (after implementation) | #DIV/0!
| Benchmarking Results Per Year |  |  | Assessment results Per Year
| Technical Potential for Efficiency Improvement: |  |  | Potential for Efficiency Improvement:
| Electricity (kWh saved/year) | -3194.1383 | #DIV/0! | Electricity (kWh saved/year) | #DIV/0! | #DIV/0!
| Fuel (MBtu saved/year) | 0 | #DIV/0! | Fuel (MBtu saved/year) | #DIV/0! | #DIV/0!
| Primary Energy (MBtu saved/year) | -23.6922 | #DIV/0! | Primary Energy (MBtu saved/year) | #DIV/0! | #DIV/0!
| Water (Gallons saved/year) | 0 | #DIV/0! | Water (Gallons saved/year) | #DIV/0! | #DIV/0!
| Net Operation Cost Reduction: |  |  | Economics:
| Electricity ($/year) | #DIV/0! | /year | Electricity Savings ($/year) | #DIV/0!
| Fuel ($/year) | #DIV/0! | /year | Fuel Savings ($/year) | #DIV/0!
| Energy - Total ($/year) | #DIV/0! | /year | Water Savings ($/year) | #DIV/0!
| Water ($/year) | #DIV/0! | /year | Capital Costs ($/year) | #DIV/0!
| Total Cost Reduction ($/year) | #DIV/0! | /year | Simple Payback Period (years) | #DIV/0!
| CO2 Emission Reduction Potential: |  |  | CO2 Emission Reduction Potential:
| Total (metric ton CO2/year) | #DIV/0! |  | Total (metric ton CO2/year) | #DIV/0!
| Total (metric ton C/year) | #DIV/0! |  | Total (metric ton C/year) | #DIV/0!
Note on D26: These estimates include costs, that is, they are based on savings minus costs.
Note on F20: % of total electricity
Note on F21: % of total fuels
Note on F22: % of total primary energy
Note on N20: % of total electricity
Note on N21: % of total fuels
Note on N22: % of total primary energy

## ENERGY_RESULTS (hidden)
SELF-ASSESSMENT RESULTS - ENERGY MEASURES YOU HAVE SELECTED
| Measures (Electricity) | Total Energy Savings |  | Total Costs | Payback Period
|  | (%) | (kWh/year) | ($) | (years)
| Refrigeration | #DIV/0!
| Trigeneration - Engine | #DIV/0! | 0 | #DIV/0! | #DIV/0!
| Trigeneration - Microturbine | #DIV/0! | 0 | #DIV/0! | #DIV/0!
| Reduce wattage lighting/occupancy control | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
| Monitor performance | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
| Monitor refrigerant charge | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
| Monitor suction line filters | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
| Monitor contaminants in refrigerant | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
| Tank insulation | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
| Nighttime air cooling | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
| Reduced infiltration load from door closings | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
| Building Shell - reflective roofing materials | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
| Building & pipe Insulation and Vapor Barrier Integrity | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
| Size fan and motors more efficiently | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
| Electrodialysis | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
| Cave for barrel storage | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
| Control systems/Scheduling of compressors | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
| Floating Head Pressure (FHP) control versus fixed | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
| ASD/VFD on compressor motors | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
| ASD/VFD on condenser fans | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
| Install automatic purgers on evaporative condensers | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
| ASD/VFD on evaporator (air unit) fans | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
| Cycle evaporative (air unit) fans | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
| Pumping | 0%
| Maintenance & Monitoring | 0% | #DIV/0! | #DIV/0! | #DIV/0!
| Reduce Pumping Need | 0% | #DIV/0! | #DIV/0! | #DIV/0!
| Controls | 0% | #DIV/0! | #DIV/0! | #DIV/0!
| Correct Sizing of Pump | 0% | #DIV/0! | #DIV/0! | #DIV/0!
| Correct Sizing of Piping | 0% | #DIV/0! | #DIV/0! | #DIV/0!
| Efficient Pump Designs | 0% | #DIV/0! | #DIV/0! | #DIV/0!
| Precision castings, coatings, polishings | 0% | #DIV/0! | #DIV/0! | #DIV/0!
| Multiple Pumps | 0% | #DIV/0! | #DIV/0! | #DIV/0!
| Trimming Impeller | 0% | #DIV/0! | #DIV/0! | #DIV/0!
| Adjustable Speed Drive | 0% | #DIV/0! | #DIV/0! | #DIV/0!
| Replace V-Belts | 0% | #DIV/0! | #DIV/0! | #DIV/0!
| Compressed Air | 0%
| Maintenance & Monitoring | 0% | #DIV/0! | #DIV/0! | #DIV/0!
| Repair Leaks | 0% | #DIV/0! | #DIV/0! | #DIV/0!
| Reduce Pressure Drop | 0% | #DIV/0! | #DIV/0! | #DIV/0!
| Reduce Compressed Air Usage | 0% | #DIV/0! | #DIV/0! | #DIV/0!
| Controls | 0% | #DIV/0! | #DIV/0! | #DIV/0!
| Reduce Inlet Temperature | 0% | #DIV/0! | #DIV/0! | #DIV/0!
| Adjustable Speed Drives | 0% | #DIV/0! | #DIV/0! | #DIV/0!
| Correct Sizing of Piping | 0% | #DIV/0! | #DIV/0! | #DIV/0!
| Heat Recovery for Water Heating | 0% | #DIV/0! | #DIV/0! | #DIV/0!
| Replace V-Belt Drives | 0% | #DIV/0! | #DIV/0! | #DIV/0!
| Reduce Air Compressor Discharge Pressure | 0% | #DIV/0! | #DIV/0! | #DIV/0!
| Motors | 0%
| Maintenance & Monitoring | 0% | #DIV/0! | #DIV/0! | #DIV/0!
| Correct Sizing of Motor | 0% | #DIV/0! | #DIV/0! | #DIV/0!
| High-Efficiency Motors | 0% | #DIV/0! | #DIV/0! | #DIV/0!
| Adjustable Speed Drive | 0% | #DIV/0! | #DIV/0! | #DIV/0!
| Replace V-Belts | 0% | #DIV/0! | #DIV/0! | #DIV/0!
| Lighting | 0%
| Switch off lights when non-occupied | 0% | #DIV/0! | #DIV/0! | #DIV/0!
| Replace Incandescents by CFLs | 0% | #DIV/0! | #DIV/0! | #DIV/0!
| Replace Magnetic by Electronic Ballasts | 0% | #DIV/0! | #DIV/0! | #DIV/0!
| Replace T-12 by T-8 Tubes | 0% | #DIV/0! | #DIV/0! | #DIV/0!
| Replace HID-lights by T-5 Hi-Bay Lighting | 0% | #DIV/0! | #DIV/0! | #DIV/0!
| Replace Mercury lights by High-Press Sodiums | 0% | #DIV/0! | #DIV/0! | #DIV/0!
| Reduce Voltage of HID Lights | 0% | #DIV/0! | #DIV/0! | #DIV/0!
| Replace Exit signs by LED exit Signs | 0% | #DIV/0! | #DIV/0! | #DIV/0!
| Install Lighting controls | 0% | #DIV/0! | #DIV/0! | #DIV/0!
| Install Daylighting | 0% | #DIV/0! | #DIV/0! | #DIV/0!
| Miscellaneous - Electric | #DIV/0!
| Energy Management Systems | 0% | 0 | 0 | #DIV/0!
| Efficient Transformers | 0% | 0 | 0 | #DIV/0!
| Power Factor Correction Systems | 0% | 0 | 0 | #DIV/0!
| Power Management Office Equipment | 0% | #DIV/0! | #DIV/0! | #DIV/0!
| Electronic controls to turn off equipment | 0% | #DIV/0! | #DIV/0! | #DIV/0!
| Anaerobic Digestion | 0% | #DIV/0! | #DIV/0! | #DIV/0!
| Photovoltaics | #DIV/0! | 0 | 0 | #DIV/0!
| Combined Heat and Power (CHP) | #DIV/0!
| Cogeneration - Engine | #DIV/0! | 0 | #DIV/0! | #DIV/0!
| Cogeneration - Microturbine | #DIV/0! | 0 | #DIV/0! | #DIV/0!
| Trigeneration - Engine | #DIV/0! | 0 | #DIV/0! | #DIV/0!
| Trigeneration - Microturbine | #DIV/0! | 0 | #DIV/0! | #DIV/0!
| Measures (Fuel) | Total Energy Savings |  | Total Costs | Payback Period
|  | (%) | (MBtu/year) | ($) | (years)
| Hot Water | 0
| Ozone Cleaning Barrels | 0% | #DIV/0! | 0 | 0
| Improved Boiler Maintenance | 0% | #DIV/0! | #DIV/0! | #DIV/0!
| Reduce Flue Gas Volume | 0% | #DIV/0! | #DIV/0! | #DIV/0!
| Reduce Excess Inlet Air | 0% | #DIV/0! | #DIV/0! | #DIV/0!
| Correct Sizing of Boiler | 0% | #DIV/0! | #DIV/0! | #DIV/0!
| Improve Insulation of Boiler | 0% | #DIV/0! | #DIV/0! | #DIV/0!
| Solar Water Heating | 0% | #DIV/0! | #DIV/0! | #DIV/0!
| Return Condensate/Used Water | 0% | #DIV/0! | #DIV/0! | #DIV/0!
| Relocate Boiler | 0% | #DIV/0! | #DIV/0! | #DIV/0!
| Repair Leaks in Distribution Piping | 0% | #DIV/0! | #DIV/0! | #DIV/0!
| Maintain Insulation Hot Water Piping | 0% | #DIV/0! | #DIV/0! | #DIV/0!
| Insulate Hot Water Distribution Pipes | 0% | #DIV/0! | #DIV/0! | #DIV/0!
| Heat exchanger replaces tank water heating | 0% | #DIV/0! | #DIV/0! | #DIV/0!
| Miscellaneous - Fuels | 0%
| Weekend setback temperatures | 0% | #DIV/0! | #DIV/0! | #DIV/0!
Note on J2: This button compresses the chart to the left, according to what measures you have selected (or just re-selected).

## WATER_RESULTS (hidden)
SELF-ASSESSMENT RESULTS - WATER MEASURES YOU HAVE SELECTED
| Measure | Total Water Savings |  | Total Costs | Payback Period
|  | (%) | (Gal/year) | ($) | (years)
| General Water Measures | 0%
| Water Management Program | 0% | #DIV/0! | #DIV/0! | #DIV/0!
| Repair Leaks | 0% | #DIV/0! | #DIV/0! | #DIV/0!
| General Cleaning | #DIV/0!
| Sweeping floors before water washing | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
| High Pressure nozzles with automatic shutoff devices | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
| Barrel Cleaning | #DIV/0!
| High pressure nozzle - tank cleaning | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
| Ozone tank cleaning of barrels | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
| Automatic cleaning systems | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
| Cooling Tower | #DIV/0!
| Alternative sources of make-up water | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
| Replace single pass cooling system with cooling tower | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
| Reduce bleed off in cooling tower | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
| Operate bleed off continuously/install controls | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
| Evaporative Cooling | #DIV/0!
| Replace non-recirculating evaporative coolers | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
| Reuse bleed-off water in evaporative cooling | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
| Hot Water | #DIV/0!
| Reduction of make-up water by reduction in energy use | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
| Return Condensate/Used Water | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
| Humidifiers | #DIV/0!
| Controls and water supply valves | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
| Efficient humidifier models | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
| Caves for barrel storage | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
| Miscellaneous | #DIV/0!
| Efficient toilets and building appliances | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
END OF PROGRAM
(Push Control + PAGE-UP to go back to former sheets)
(Press References Button to Go to References Sheet)
Note on H3: This button compresses the chart to the left, according to what measures you have selected (or just re-selected).

## References (hidden)
References
AgStar. 2004. AgStar Program. URL: http://www.epa.gov/agstar/
Baen, P. R. and R. E. Barth. (1994). Insulate Heat Tracing Systems Correctly. Chemical Engineering Progress. September: 41-46.
Barnish, T. J., M. R. Muller, and D. J. Kasten (1997). Motor Maintenance: A Survey of Techniques and Results. ACEEE Summer Study on Energy Efficiency in Industry
July 8-11, 1997, Saratoga Springs, NY.
Best Practice Programme. (1996a). General Information Report 41: Variable Flow Control. Available for download at http://www.energy-efficiency.gov.uk/index.cfm
Best Practice Programme. (1996b). Good Practice Case Study 300: Energy Savings by Reducing the Size of a Pump Impeller. Available for download at http://www.energy-efficiency.gov.uk/index.cfm.
Best Practice Programme. (1998). Good Practice Guide 249: Energy Savings in Industrial Water Pumping Systems. Available for download at http://www.energy-efficiency.gov.uk/index.cfm
Black, G. (2002). Above Ground “Caves,” Icons of the California Wine Country. Vineyard & Winery Management. Jan/Feb: 1-4.
Boulton, R.B., V.L. Singleton, L.F. Bisson and R.E. Kunkee. 1996. Principles and Practices of Winemaking. New York, NY: Chapman & Hall.
Caffal, C. (1995). Energy Management in Industry. Centre for the Analysis and Dissemination of Demonstrated Energy Technologies (CADDET), the Netherlands. Analyses series 17, December.
California Energy Commission (CEC) and the Office of Industrial Technologies (OIT), Energy Efficiency and Renewable Energy, U. S. Department of Energy. (2002). Case Study: Pump System Controls Upgrade Saves Energy at a Network Equipment Manufacturing Company's Corporate Campus. January.
California Sustainable Winegrowing Alliance (CSWA) (2004). Wine Community Sustainability Report. Winery Water Conservation and Water Quality: Chapter 10.
Canadian Industry Program for Energy Conservation (CIPEC). (2001). Boilers and Heaters, Improving Energy Efficiency. Natural Resources Canada, Office of Energy Efficiency. August.
Castellow, C., C. E. Bonnyman, H. G. Peach, J. C. Ghislain, P. A. Noel, M. A. Kurtz, J. Malinowski, and M. Kushler. (c. 1997). Energy Efficiency in Automotive and Steel Plants.
Centre for the Analysis and Dissemination of Demonstrated Energy Technologies (CADDET). (1994). High Efficiency Motors for Fans and Pumps. Case study UK94.502/2B.FO5.
Centre for the Analysis and Dissemination of Demonstrated Energy Technologies (CADDET). (1997a). Saving Energy with Efficient Compressed Air Systems. Maxi Brochure 06.
Centre for the Analysis and Dissemination of Demonstrated Energy Technologies (CADDET). (1997b). Energy Savings with New Industrial Paint Drying and Baking Oven. Case study CA97.504/2X.F06.
Centre for the Analysis and Dissemination of Demonstrated Energy Technologies (CADDET). 2001. Saving Energy with Daylighting Systems. Maxi Brochure 14 (www.caddet.org).
Coggan, M. 2004. Cogeneration at Vineyard 29: Generating Power, and Peace-of-Mind, Saving Money and the Environment. Vineyard & Winery Management 1 30 (January 2004).
Cole, G. C. (1998). Pharmaceutical Production Facilities: Design and Applications. 2nd Edition. Taylor & Francis, NY, NY.
Cook, B. 1998. High-efficiency Lighting in Industry and Commercial Buildings. Power Engineering Journal. October: pp.197-206.
Copper Development Association (CDA). (2000). Cummins engine company saves $200,000 per Year with Energy-Efficient Motors. Case Study A6046.
Copper Development Association (CDA). (2003). Energy Efficiency Case Study: Brass Mill Cuts Costs with NEMA Premium™ Motors. Available at: http://www.copper.org/applications/electrical/energy/Brass_Mill_Cuts_Cost_A6089.html
Dahlberg, E. (2004). Personal written communication with Eric Dahlbert of WineSectets, a manufacturer of electrodialysis equipment. December 6, 2004.
Dettmers, Dan, 2004. Personal communication with Dan Dettmers, Wisconsin Energy Center, November 2004.
Department of Energy (DOE). (2001a). Office of Industrial Technologies, Energy Efficiency and Renewable Energy. Best Practices Program. Information on steam. http://www.oit.doe.gov/ bestpractices/steam/
Department of Energy (DOE). (2001b). Office of Industrial Technologies, Energy Efficiency and Renewable Energy. Best Practices Program. Information on steam. http://www.oit.doe.gov/ bestpractices/steam/
Department of Water Resources, California. (2004). Water Efficiency Guide for Business Managers and Facility Engineers. October. Available at http://www.owue.water.ca.gov/docs/water_efficiency_guide.pdf
Easton Consultants, Inc. (1995). Strategies to Promote Energy-Efficient Motor Systems in North America's OEM Markets. Stamford, CT.
Efficiency Partnership (EP), (2004), “ Industrial Product Guide – Manufacturing and Processing Equipment: Motors ”, http://www.fypower.com/ind/tools/ products_results.html?id=100201.
Eley, C. and T. M. Tolen, of Eley Associates; J. R. Benya of Luminae Souter Lighting Design; F. Rubinstein and R. Verderber of Lawrence Berkeley Laboratory. 1993. Advanced Lighting Guidelines: 1993. Prepared for the Department of Energy (DOE), California Energy Commission (CEC) and Electric Power Research Institute (EPRI).
Elliot, R.N. (1995). Energy Efficiency in Electric Motor Systems. Washington, DC; American Council for an Energy Efficient Economy.
Environmental Protection Agency (EPA). 2001. Green Lights Program (Part of the ENERGY STAR Program). http://www.epa.gov/Region7/specinit/p2/volprog/estrans.htm
European Environmental Press. (2000). Conservation of Europe's Water. Mini Guide to European Initiatives. Developed with support from the European Commission's Directorate-General Environment. Available at: http://www.eep.org/miniguides/MINI_ANG/EAU_ENG/an_ea_01-32.pdf. Accessed 4/2005.
Fetters, J.L. 2002. Transformer Efficiency. Energy User News, posted on 4/23/2002. URL: www.energyusernews.com
Fetzer. (2004). Personal communication with various winemakers and operators on winemaking characteristics and energy use and savings.
Franson, P. (2000). Northwest Wineries Dig Caves, Too: New Technology Addresses Soil and Water Challenges. Wine Business Monthly (May 2000): 43-46.
Ganapathy, V. (1994). Understand Steam Generator Performance. Chemical Engineering Progress. December.
General Motors (GM). (2001). Resource Conservation/Pollution Prevention/Energy Management. General Motors website. http://www.gm.com/company/environment or http://www.gm.com/company/gmability/environment/env_annual_report/ehsreport/html/sec07/content03.htm
Goldstein, L., B. Hedman, G. Knowles, S.I. Freedman, R. Woods and T. Schweizer. 2003. Gas-Fired Distributed Energy Resource Technology Characterizations. National Renewable Energy Laboratory, Boulder, CO (Report NREL/TP-620-34783).
Griffin, B. (2000). The Enbridge Consumers Gas "Steam Saver" Program ("as found" performance and fuel savings projects from audits of 30 steam plants). In: Twenty-second National Industrial Energy Technology Conference Proceedings. Houston, Texas. April 5-6: 203-213.
Hall, L.S. 1999. Pinot Noir Producers go with the Flow, Winemakers Benefit from Using Gravity in Cellar. Wine Business Monthly, September 1999, pp.43-46.
Hovstadius, G. of ITT Fluid Technology Corporation. (2002). Personal communication.
Howe, B. and B. Scales. (1995). Assessing Processes for Compressed Air Efficiency. E Source Tech Update. November.
Hydraulic Institute. (1994). Efficiency Prediction Method for Centrifugal Pumps. Parsippany, NJ.
Hydraulic Institute and Europump. (2001). Pump Life Cycle Costs: A Guide to LCC Analysis for Pumping Systems. Parsippany, NJ.
Hydraulic Institute. (2002). Website, http://www.pumps.org/.
Industrial Assessment Center (IAC). (2001). Industrial Assessment Center Database version 8.1. http://oipea-www.rutgers.edu/database/db_f.html
Ingersoll Rand. (2001). Air Solutions Group-Compressed Air Systems Energy Reduction Basics. http://www.air.ingersoll-rand.com/NEW/pedwards.htm. June 2001.
Jekel, Todd. 2004a. Variable Frequency Drive Opportunities in Industrial Refrigeration Systems, VFD Opportunity I: Condenser Fans. The Cold Front (Vol.4 No. 2), newsletter for the Industrial Refrigeration Consortium at the University of Wisconsin. http://www.irc.wisc.edu, July.
Jekel, Todd. 2004b. Variable Frequency Drive Opportunities in Industrial Refrigeration Systems, VFD Opportunity II: Screw compressors. The Cold Front (Vol.4 No. 3), newsletter for the Industrial Refrigeration Consortium at the University of Wisconsin http://www.irc.wisc.edu, September.
Jekel, Todd. 2004c. Variable Frequency Drive Opportunities in Industrial Refrigeration Systems, VFD Opportunity III: Evaporator Fans. The Cold Front (Vol.4 No. 4), newsletter for the Industrial Refrigeration Consortium at the University of Wisconsin http://www.irc.wisc.edu, December.
Konopacki, S., H. Akbari, L. Gartland and L. Rainer. (1998). Demonstration of Energy Savings of Cool Roofs. Lawrence Berkeley National Laboratory Report LBNL-40673. Berkeley, CA.
Lawrence Berkeley National Laboratory (LBNL) and Resource Dynamics Corporation. (1998). Improving Compressed Air System Performance, a Sourcebook for Industry. Prepared for the U.S. Department of Energy, Motor Challenge Program.
Lawrence Berkeley National Laboratory (LBNL), Resource Dynamics Corporation and the Hydraulic Institute. (1999). Improving Pumping System Performance: A Sourcebook for Industry. Prepared for the U.S. Department of Energy Motor Challenge Program.
Leue, Dave, 2004. Personal communication with Dave Leue, PG&E Senior Project Manager, November 2004.
Lighting Research Center (LRC). 2001. Lighting Futures. LEDs: From Indicators to Illuminators? 3(4): http://www.lrc.rpi.edu/Futures/LF-LEDs/index.html
Martin, N., M. Ruth, and L. Price, R. N. Elliott, A. M. Shipley, and J. 2000. Emerging Energy-Efficient Industrial Technologies. Berkeley, CA: Lawrence Berkeley National Laboratory.
National Electrical Manufacturers Association (NEMA). (2001). http://www.nema.org.
North Carolina Department of Environment and Natural Resources Division of Pollution Prevention and Environmental Assistance (2005). Website: http://www.p2pays.org/
Oland, C.B. 2004. Guide to Combined Heat and Power Systems for Boiler Owners and Operators. Oak Ridge, TN: Oak Ridge National Laboratory.
Papar, Riyaz 2004. Personal communication with Riyaz Papar, private energy consultant, November 2004.
Parekh, P. (2000). Investment Grade Compressed Air System Audit, Analysis and Upgrade. In: Twenty-second National Industrial Energy Technology Conference Proceedings. Houston, Texas. April 5-6: 270-279.
Phillips, C. 2002. Pump Roundup Wine Business Monthly, September 2002, pp.24-25.
Price, A. and M.H. Ross. (1989). Reducing Industrial Electricity Costs - an Automotive Case Study. The Electricity Journal. July: 40-51.
Quinn, B. 2002. New Technology Slashes Cost and Sludge. Pollution Engineering, February 2002.
Radgen, P. and E. Blaustein (eds.). (2001). Compressed Air Systems in the European Union, Energy, Emissions, Savings Potential and Policy Actions. Germany.
Roberson, J. A., C. A. Webber, M. C. McWhinney, R. E. Brown, M. J. Pinckard, and J. F. Busch. (2004). After-hours Power Status of Office Equipment and Inventory of Miscellaneous Plug-Load Equipment. Lawrence Berkeley National Laboratory, Berkeley CA. LBNL-53729. Available at: http://enduse.lbl.gov/info/Pubs03_04.html
Scales, B. (2002). Personal written communication.
Scott, Doug, 2004. Personal communication with Doug Scott, PG&E Consultant, November 2004.
Scott, W. L and W. D. Leech (2004). Wine Caves Beneath the Northern California Vineyards. Tunnel Business Magazine, February 2004.
Southern California Edison (SCE). (2003) "Saving Money with Motors in Pharmaceutical Plants".
Toyota 2002. Personal communication with Brad Reed, Toyota Motor Manufacturing Nort America, Inc. May 2002.
Tutterow, V. (1999). Energy Efficiency in Pumping Systems: Experience and Trends in the Pulp and Paper Industry. American Council for an Energy Efficient Economy (ACEEE).
Tutterow, V., D. Casada and A. McKane. (2000). "Profiting from your Pumping System," In Proceedings of the Pump Users Expo 2000. September. Louisville, KY: Pumps & Systems Magazine and Randall Publishing Company.
U. S. Department of Energy, Office of Industrial Technologies (OIT). (2002a). Pumps: Cost Reduction Strategies. Available at the website www.oit.doe.gov/bestpractices.
Vickers, A. (2001). Handbook of Water Use and Conservation. WaterPlow Press: Amherst, MA.
Wine Institute 2002. Sustainable Winegrowing Practices August 2002.
Worrell, E., J.W. Bode, J.G. de Beer, 1997. "Energy Efficient Technologies in Industry - Analysing Research and Technology Development Strategies - The 'Atlas' Project", Dept. of Science, Technology & Society, Utrecht University, Utrecht, The Netherlands.
Xenergy, Inc. (1998). United States Industrial Electric Motor Systems Market Opportunities Assessment. U.S. Department of Energy's Office of Industrial Technology and Oak Ridge National Laboratory. Massachusetts.
Zeitz, Ronald A. ed. 1997. CIBO Energy Efficiency Handbook. Council of Industrial Boiler Owners, Burke, Virginia.

## Pumping (hidden)
PUMPING ENERGY USE: CALCULATION OF BENCHMARK ENERGY USE
Production (from input sheet): | Red | White-sweet | White-tank | White-Barrel fermented | Total
Wine produced annually (cases) | 0 | 0 | 0 | 0 | 0
Wine bottled annually (cases) | 0 | 0 | 0 | 0 | 0
Pumping Energy Use:
Cooling water (kWh) |  |  |  |  | 0
Hot water malolactic (kWh) |  |  |  |  | 0
Hot water for cleaning - white bbl rm (kWh) |  |  |  | 0 | 0
Hot water for cleaning - red bbl rm (kWh) | 0 |  |  |  | 0
Hot water for cleaning - bottling (kWh) |  |  |  |  | 0
To/from waste/wells (kWh) |  |  |  |  | 0
Wine pumping (kWh) | 0 | 0 | 0 | 0 | 0
Wastewater aeration (kWh) |  |  |  |  | 0
Total pumping energy (kWh) |  |  |  |  | 0
Benchmark Pumping Energy Use:
Specific energy use (kWh/case produced) |  |  |  |  | #DIV/0!
ADAPTED: 7/1/04
Sheet to be hidden

## Receiving (hidden)
RECEIVING: CALCULATION OF BENCHMARK ENERGY USE
Grapes received (from input sheet): | Red | White-sweet | White-tank | White-Barrel fermented | Total
Grapes received annually (tons) | 0 | 0 | 0 | 0 | 0
Time equipment runs annually (Days) | 60 | 60 | 60 | 60 | 60
Time equipment runs annually (hrs/day) | 15 | 15 | 15 | 15 | 15
Time equipment runs annually (hrs) | 900 | 900 | 900 | 900 | 900
Receiving Energy Use:
Unloading (kWh): | 0 | 0 | 0 | 0 | 0
Pumping & Moving (kWh): | 0 | 0 | 0 | 0 | 0
Total (kWh) | 0 | 0 | 0 | 0 | 0
Benchmark Receiving Energy Use:
Specific energy use (kWh/ton) |  |  |  |  | #DIV/0!
Specific energy use (kWh/case) |  |  |  |  | #DIV/0!
ADAPTED 7/1/04
Sheet to be hidden

## Pressing (hidden)
PRESSING: CALCULATION OF BENCHMARK ENERGY USE
Grapes pressed (from input sheet): | Red | White-sweet | White-tank | White-Barrel fermented | Total
Grapes received annually (tons) | 0 | 0 | 0 | 0 | 0
Time equipment runs annually (Days) | 60 | 60 | 60 | 60 | 60
Time equipment runs annually (hrs/day) | 15 | 15 | 15 | 15 | 15
Time equipment runs annually (hrs) | 900 | 900 | 900 | 900 | 900
Energy use for Pressing:
Pressing (kWh) | 0 | 0 | 0 | 0 | 0
Pumping (kWh) | 0 | 0 | 0 | 0 | 0
Total Pressing (kWh) | 0 | 0 | 0 | 0 | 0
Benchmark Energy Use Pressing:
Specific energy use (kWh/ton) |  |  |  |  | #DIV/0!
Specific energy use (kWh/case) |  |  |  |  | #DIV/0!
ADAPTED 7/1/04
Sheet to be hidden

## Fermentation (hidden)
FERMENTATION: CALCULATION OF BENCHMARK ENERGY USE
reaction | ΔH (reaction)= 4.77 kJ/L Brix * sugar content * Volume
tanks | ΔH (cooling down to Ferm. Temp) = Cp * ρ * ΔTemp * Volume
tanks | ΔH (conductive losses) = k * Surface Area jackets* ΔT(room-glycol) * time
tanks | ΔH (conductive losses) = k * Surface Area non-jackets* ΔT(room-ferm) * time
room | ΔH (cooling) = Cp * ρ * ΔTemp * Volume
room - infiltration | ΔH (cooling) = Cp * ρ * ΔTemp * Volume
room | ΔH (conductive losses - walls & roof) = k * Surface Area* ΔTemp * time
| 1 kcal= | 4.18 | kJ
Calculation Energy Use Fermentation | Red | White-sweet | White-tank | White-Barrel fermented | Total
Fermenting Temperature (ºF) | 77.5 | 49 | 59 | 56.5
Fermenting Temperature (ºC) | 25.2778 | 9.4444 | 15 | 13.6111
Juice Temperature (ºC) | 11.9 | 11.9 | 11.9 | 11.9
Average Room Temperature (ºF) | 57 | 45.25 | 45.25 | 58.53
Average Room Temperature (ºC) | 13.8889 | 7.3611 | 7.3611 | 14.7389
Average Ambient Temperature (ºC) | 11.9 | 11.9 | 11.9 | 11.9
Glycol cooling Temperature (ºF) | 67.5 | 39 | 49 | 46.5
Glycol Cooling Temperature (ºC) | 19.7222 | 3.8889 | 9.4444 | 8.0556
Roof Temperature (ºC) | 16.9 | 16.9 | 16.9 | 16.9
Heat Capacity juice (Cp, kJ/kg ºC) | 3.8 | 3.8 | 3.8 | 3.8
Density juice (ρ, kg/L) | 1.09 | 1.095 | 1.09 | 1.095
Heat Capacity air (Cp, kJ/kg K) | 1 | 1 | 1 | 1
Density air (ρ, kg/L) | 0.00129 | 0.00129 | 0.00129 | 0.00129
Surface Heat Transfer Coefficient (air) (k, W/m2ºC) | 8.29 | 8.29 | 8.29 | 8.29
Surface Heat Transfer Coefficient (air) (k, kJ/m2ºC hr) | 29.844 | 29.844 | 29.844 | 29.844
Room dimensions - square footage (roof area, ft2) | 0 | 0 | 0 | N/A | 0
- height (ft) | 26 | 26 | 26 | N/A | 26
- outside perimeter (ft) | 278 | 245 | 278 |  | 801
- area of outside walls (ft2) | 7228 | 6370 | 7228 |  | 20826
- square meterage (roof area, m2) | 0 | 0 | 0 |  | 0
- height (m) | 7.9248 | 7.9248 | 7.9248 |  | 7.9248
- outside perimeter (m) | 84.7344 | 74.676 | 84.7344 |  | 244.1448
- area of outside walls (m2) | 671.5032 | 591.7924 | 671.5032 |  | 1934.7987
Volume of room (ft3) | 0 | 0 | 0 | N/A | 0
Volume of room (L) | 0 | 0 | 0 |  | 0
Conductivity of walls (k, kJ/m2ºC hr) | 1.877 | 1.877 | 1.877 |  | 1.877
Conductivity of roof (k, kJ/m2ºC hr) | 0.938 | 0.938 | 0.938 |  | 0.938
Air exchanges - CO2 exhaust fans (ft3/hr) | 0 | 0 | 0 |  | 0
Air exchanges - leaks (ft3/hr) | 0 | 0 | 0 |  | 0
Air exchanges -CO2 exhaust fans (L/hr) | 0 | 0 | 0 |  | 0
Air exchanges - leaks (L/hr) | 0 | 0 | 0 |  | 0
Fermentation time (Days) | 8.5 | 28 | 14 | 7
Fermentation time (Hours) | 204 | 672 | 336 | 168
Sugar Content (Brix) | 24 | 21.5 | 23.5 | 23.5 |  | total tank whites: | sweet tank: | dry tank:
Annual production (Juice fermented) (Gallons) | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
Annual production (Juice fermented) (Liters) | 0 | 0 | 0 | 0 | 0 | 0
Capacity utilization during fermentation | 0.874 | 0.874 | 0.874 | 0.874
Vessel dimensions - height (m) | 5.5 | 5.5 | 5.5
- diameter (m) | 3.1 | 3.1 | 3.1
- thickness (m) | 0.002 | 0.002 | 0.002
Surface Area (m2) | 61.1118 | 61.1118 | 61.1118
Volume (m3) | 41.5122 | 41.5122 | 41.5122
Volume (L) | 41512.2199 | 41512.2199 | 41512.2199
Energy for heat of reaction (kJ) | 0 | 0 | 0 |  | 0
Energy for cooling incoming juice (kJ) | 0 | 0 | 0 | 0 | 0
Energy for conductive losses tank (kJ) | 0 | 0 | 0 |  | 0
Energy for conductive losses tank (kJ) | 0 | 0 | 0
Energy for cooling room (kJ) | 0 | 0 | 0 |  | 0
Infiltration losses (kJ) | 0 | 0 | 0 |  | 0
Energy for conductive losses - from walls (kJ) | -5414727.6147 | 10890227.0106 | 12357073.9141 |  | 17832573.31
Energy for conductive losses - from roof (kJ) | 0 | 0 | 0 |  | 0
Sub-Total Energy for fermentation (kJ) | -5414727.6147 | 7296452.0971 | 8279239.5224 | 0 | 10160964.0048
Coefficient of Performance (COP, W/W) | 4.1 | 4.1 | 4.1 | 4.1
Total Energy for fermentation (kJ) | -1320665.2719 | 1779622.4627 | 2019326.7128 | 0 | 2478283.9036
Total Energy used in fermentation (kBtu): | -1251.9907 | 1687.0821 | 1914.3217 | 0 | 2349.4131
Total Energy used in fermentation (kWh) | -366.8515 | 494.3396 | 560.9241 | 0 | 688.4122
REVISED: 7/7/2004
To be hidden
Note on A21: Based on standard operating practices assumed to be 10 degree C less than the fermentation temperature.
Note on A42: Leaks: estimated to be 50% of the room volume per hour, based on typical commercial and residential buildings.
Note on A60: ΔH (conductive losses) = k * Surface Area jackets* ΔT(room-glycol) * time Capacity = 87.4% full, hence, the multiplier 0.874 (Cell B-E51) is the capacity utilization factor About 53% of tanks are covered by jackets.
Note on A61: ΔH (conductive losses) = k * Surface Area non-jackets* ΔT(room-ferm) * time
Note on A68: Christina Galitsky: A best winery saves 33% by insulating tanks.
Note on B5: Christina Galitsky: time is calculated based on volume of one tank and total volume needing to be fermented - it also needs to take into account capacity (and the fact that tanks aren't at full capacity always). SA of the jackets are estimated to be 53% of total surface area. Non-jackets are 47%.
Note on B6: Christina Galitsky: time is calculated based on volume of one tank and total volume needing to be fermented - it also needs to take into account capacity (and the fact that tanks aren't at full capacity always). SA of the jackets are estimated to be 53% of total surface area. Non-jackets are 47%.
Note on B19: This number is pulled up from the database containing temperature data for each winery region.
Note on B22: This number is pulled up from the database containing temperature data for each winery region.
Note on C16: This number is pulled up from the database containing temperature data for each winery region.
Note on C19: This number is pulled up from the database containing temperature data for each winery region.
Note on C22: This number is pulled up from the database containing temperature data for each winery region.
Note on D19: This number is pulled up from the database containing temperature data for each winery region.
Note on E19: This number is pulled up from the database containing temperature data for each winery region.

## Malolactic_fermentation (hidden)
MALOLACTIC FERMENTATION: CALCULATION OF BENCHMARK ENERGY USE
ΔH (reaction)= negligible
ΔH (heating) = Cp * ρ * ΔTemp * Volume
ΔH (conductive losses) = k * Surface Area * ΔTemp * time
| 1 kcal= | 4.18 | kJ
Calculation Benchmark Energy Use | Red | White-sweet | White-tank | White-Barrel fermented
Fermenting Temperature ( ºF) | 70 | 70 | 70 | 78
Fermenting Temperature ( ºC) | 21.1111 | 21.1111 | 21.1111 | 25.5556
Average Ambient Temperature (ºC) | 5.4 | 5.4 | 5.4 | 5.4
Heat Capacity (Cp, kJ/kg ºC) | 4.5 | 4.5 | 4.5 | 4.5
Density (ρ, kg/L) | 0.99 | 0.99 | 0.99 | 0.99
Surface Heat Transfer Coefficient (air) (k, W/m2ºC) | 8.29 | 8.29 | 8.29 | 8.29
Surface Heat Transfer Coefficient (air) (k, kJ/m2ºC hr) | 29.844 | 29.844 | 29.844 | 29.844
Fermentation time (Days) | 45 | 56 | 56 | 56
Fermentation time (Hours) | 1080 | 1344 | 1344 | 1344
Annual production (Gallons) undergoing malolactic | 0 | 0 | 0 | 0
Annual production (Liters) undergoing malolactic | 0 | 0 | 0 | 0
Room dimensions - average height |  |  |  | 24
- square footage |  |  |  | 7312.5
Insulation Walls (R-value) |  |  |  | R-30
Insulation Roof (R-value) |  |  |  | R-13
Vessel dimensions - height (m) | 5.5 | 5.5 | 5.5
- diameter (m) | 3.1 | 3.1 | 3.1
- thickness (m) | 0.002 | 0.002 | 0.002
Surface Area (m2) | 61.1118 | 61.1118 | 61.1118
Volume (m3) | 41.5122 | 41.5122 | 41.5122
Volume (L) | 41512.2199 | 41512.2199 | 41512.2199
Energy for heating (MJ) | 0 | 0 | 0 |  | 0
Energy for conductive losses (MJ) | 0 | 0 | 0 |  | 0
Propane used for heating (MJ) |  |  |  | 0
Electricity use of fans (kWh) |  |  |  | 0
Total Energy for fermentation (kJ) | 0 | 0 | 0 | 0 | 0
Total Electricity Use (kWh) | 0 | 0 | 0 | 0 | 0
Total Fuel Use (MBtu) | 0 | 0 | 0 | 0 | 0
REVISED 7/7/2004
Sheet to hidden
Note on A12: This number is pulled up from a list containing temperature data for each winery region.

## Clarification&Stabilization (hidden)
COLD STABILIZATION: CALCULATION OF BENCHMARK ENERGY USE
tanks | ΔH (cooling down to Stab. Temp) = Cp * ρ * ΔTemp * Volume
tanks | ΔH (conductive losses) = k * Surface Area jackets* ΔT(room-glycol) * time
tanks | ΔH (conductive losses) = k * Surface Area non-jackets* ΔT(room-c.s. temp) * time
room | ΔH (cooling) = Cp * ρ * ΔTemp * Volume
room - infiltration | ΔH (cooling) = Cp * ρ * ΔTemp * Volume
room | ΔH (conductive losses - walls & roof) = k * Surface Area* ΔTemp * time
| 1 HP = | 0.07457 | kW
Cold Stabilization - Benchmark Energy Use | Red | White-sweet | White-tank | White-Barrel fermented | Total
Heat Capacity (Cp, kJ/kg ºC) | 4.5 | 4.5 | 4.5 | 4.5 | 4.5
Density (ρ, kg/L) | 0.99 | 0.99 | 0.99 | 0.99 | 0.99
Surface Heat Transfer Coefficient (air) (k, W/m2ºC) | 8.29 | 8.29 | 8.29 | 8.29 | 8.29
Surface Heat Transfer Coefficient (air) (k, kJ/m2ºC hr) | 29.844 | 29.844 | 29.844 | 29.844 | 29.844
Annual production (Gallons) | 0 | 0 | 0 | 0 | 0
Annual production (Liters) | 0 | 0 | 0 | 0 | 0
Vessel dimensions - height (m) | 5.5 | 5.5 | 5.5 | 5.5 | 5.5
- diameter (m) | 3.1 | 3.1 | 3.1 | 3.1 | 3.1
- thickness (m) | 0.002 | 0.002 | 0.002 | 0.002 | 0.002
Surface Area (one tank) (m2) | 61.1118 | 61.1118 | 61.1118 | 61.1118 | 61.1118
Volume (one tank) (m3) | 41.5122 | 41.5122 | 41.5122 | 41.5122 | 41.5122
Volume (one tank) (L) | 41512.2199 | 41512.2199 | 41512.2199 | 41512.2199 | 41512.2199
Heat Capacity air (Cp, kJ/kg K) | 1 | 1 | 1 | 1 | 1
Density air (ρ, kg/L) | 0.00129 | 0.00129 | 0.00129 | 0.00129 | 0.00129
Room dimensions - square footage (roof area, ft2) | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0!
- height (ft) | 26 | 26 | 26 | 26 | 26
- outside perimeter (ft) | 278 | 245 | #DIV/0! | #DIV/0! | #DIV/0!
- area of outside walls (ft2) | 7228 | 6370 | #DIV/0! | #DIV/0! | #DIV/0!
- square meterage (roof area, m2) | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0!
- height (m) | 7.9248 | 7.9248 | 7.9248 | 7.9248 | 7.9248
- outside perimeter (m) | 84.7344 | 74.676 | #DIV/0! | #DIV/0! | #DIV/0!
- area of outside walls (m2) | 671.5032 | 591.7924 | #DIV/0! | #DIV/0! | #DIV/0!
Volume of room (ft3) | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0!
Volume of room (L) | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0!
Conductivity of walls (k, kJ/m2ºC hr) | 1.877 | 1.877 | 1.877 | 1.877 | 1.877
Conductivity of roof (k, kJ/m2ºC hr) | 0.938 | 0.938 | 0.938 | 0.938 | 0.938
Air exchanges - leaks (ft3/hr) | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0!
Air exchanges - leaks (L/hr) | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0!
| Red | White-sweet | White-tank | White-Barrel fermented | Total
Wine cold stabilized (gallon) | 0 | 0 | 0 | 0 | 0
Wine cold stabilized (l) | 0 | 0 | 0 | 0 | 0
Cold Stabilization Temp ( ºF) | 26 | 26 | 26 | 26 | 26
Cold Stabilization Temp ( ºC) | -3.3333 | -3.3333 | -3.3333 | -3.3333 | -3.3333
Average Ambient Temperature (ºC) | 5.4 | 5.4 | 5.4 | 5.4 | 5.4
Temperature of incoming wine (ºC) | 25.2778 | 9.4444 | 15 | 13.6111 | #DIV/0!
Average Room Temperature (ºF) | 35.25 | 35.25 | 35.25 | 35.25 | 35.25
Average Room Temperature (ºC) | 1.8056 | 1.8056 | 1.8056 | 1.8056 | 1.8056
Glycol Cooling Temperature (ºF) | 16 | 16 | 16 | 16 | 16
Glycol Cooling Temperature (ºC) | -8.8889 | -8.8889 | -8.8889 | -8.8889 | -8.8889
Roof Temperature (ºC) | 19.7 | 19.7 | 19.7 | 19.7 | 19.7
Time (Days) | 35 | 35 | 35 | 35 | 35
Time (Hours) | 840 | 840 | 840 | 840 | 840
Energy for cooling tank (kJ) |  |  |  |  | #VALUE! | 0
Energy for conductive losses tank (kJ) |  |  |  |  | #VALUE! | 0
Energy for conductive losses tank (kJ) |  |  |  |  | #VALUE! | 0
Energy for cooling room (kJ) |  |  |  |  | #VALUE! | 0
Infiltration losses (kJ) |  |  |  |  | #VALUE! | 0
Energy for conductive losses - from walls (kJ) |  |  |  |  | #VALUE! | 0
Energy for conductive losses - from roof (kJ) |  |  |  |  | #VALUE! | 0
Sub-Total Energy in Cold Stabilization (kJ) | 0 | 0 | 0 | 0 | #VALUE! | 0
Coefficient of Performance (COP) | 3 | 3 | 3 | 3 | 3 | 3
Total Energy in Cold Stabilization (kJ) | 0 | 0 | 0 | 0 | #VALUE! | 0
Total Energy in Cold Stabilization (kWh) | 0 | 0 | 0 | 0 | #VALUE! | 0
FINING | Red | White-sweet | White-tank | White-Barrel fermented | Total
Time (Days) |  |  |  |  | 112
Time (Hours) |  |  |  |  | 2016
Energy (kWh) |  |  |  |  | 2705.9962
DIALYSIS
Time (Days)
Time (Hours) | 0 | 0 | 0 | 0
Energy (kWh) | 0 | 0 | 0 | 0 | 0
Total Energy use clarification & stabilization (kWh) | 0 | 0 | 0 | 0 | 2705.9962
revised 4/20/05
Sheet to hidden
Note on A38: Leaks: estimated to be 50% of the room volume per hour. Estimate based on typical exchange rates for warehouses, commercial buildings, and residential spaces.
Note on A46: This number is pulled up from a list containing temperature data for each winery region.
Note on A51: Based on standard practices assumed to be 10 degree C less than the cold stabilization temperature.
Note on A52: This number is pulled up from a list containing temperature data for each winery region.
Note on A57: ΔH (conductive losses) = k * Surface Area all jacketed tanks* ΔT(room-glycol) * time 0.53 is surface area of tank covered by jackets
Note on A58: ΔH (conductive losses) = k * Surface Area all non-jacketed tank area* ΔT(room-ferm) * time
Note on B4: Christina Galitsky: time is calculated based on volume of one tank and total volume needing to be fermented - it also needs to take into account capacity (and the fact that tanks aren't at full capacity always). SA of the jackets are estimated to be 53% of total surface area. Non-jackets are 47%.
Note on B5: Christina Galitsky: time is calculated based on volume of one tank and total volume needing to be fermented - it also needs to take into account capacity (and the fact that tanks aren't at full capacity always). SA of the jackets are estimated to be 53% of total surface area. Non-jackets are 47%.
Note on C53: Cold Stabilization rule of thumb: chill at -4 to -2 degrees C for a week to two weeks (Margalit, Y., 1997, pg 294).
Note on D53: Cold Stabilization rule of thumb: chill at -4 to -2 degrees C for a week to two weeks (Margalit, Y., 1997, pg 294).
Note on E53: Cold Stabilization rule of thumb: chill at -4 to -2 degrees C for a week to two weeks (Margalit, Y., 1997, pg 294).

## Aging&Storing (hidden)
CELLARS AND BARREL STORAGE: CALCULATION OF BENCHMARK ENERGY USE
Includes Barrel Fermentation for White Wines (barrel fermented)
Energy Use | Red | White-sweet | White-tank | White-Barrel fermented | Total
Cooling (kWh) | 0 |  |  | 0 | 0
Fan (kWh) | 0 |  |  | 0 | 0
Total (kWh) | 0 |  |  | 0 | 0
Benchmark Energy Use Barrel Storage
Specific Electricity Consumption (kWh/case) | #DIV/0! |  |  | #DIV/0!
ADAPTED: 7/2/2004
Sheet to be hidden
Based on calculations with DOE-2 model.
Benchmark assumption: storage in underground cellar without additional cooling needs. Only fans are required for cooling (night air) in storage rooms or caves.

## Bottling (hidden)
BOTTLING ENERGY USE: CALCULATION OF BENCHMARK ENERGY USE
Input data (from input sheet) | Red | White-sweet | White-tank | White-Barrel fermented | Total
Wine bottled annually (cases) | 0 | 0 | 0 | 0 | 0
Time equipment runs annually (Weeks) |  |  |  |  | 52
Time equipment runs annually (hrs/week) |  |  |  |  | 43.3333
Time equipment runs annually (hrs) |  |  |  |  | 2253.3333
Energy use for bottling:
Energy used in equipment (kWh): | 0 | 0 | 0 | 0 | 0
Pumping Energy (kWh): | 0 | 0 | 0 | 0 | 0
Total Energy used in Bottling (kWh): | 0 | 0 | 0 | 0 | 0
Benchmark Energy Use Bottling
Specific energy use (kWh/case) |  |  |  |  | 0
ADAPTED: 7/1/04
Sheet to be hidden

## Other (hidden)
MISCELLANEOUS ENERGY USE: CALCULATION OF BENCHMARK
Input Data (from input sheet) | Red | White-sweet | White-tank | White-Barrel fermented | Total
Production (cases) |  |  |  |  | 0
Electricity Uses
Lighting (kWh) |  |  |  |  | 0
Office Equipment, workshops (kWh) |  |  |  |  | 0
Miscellaneous (kWh) |  |  |  |  | 0
Heat Production
Hot water production (MBtu) |  |  |  |  | 0
Wine Heating before bottling (MBtu) |  |  |  |  | 0
(Wine Heating before bottling (MBtu) - if cold stabilizing) |  |  |  |  | 0
Other Fuel Uses
Space heating and miscellaneous (MBtu) |  |  |  |  | 0
Propane for forklifts (MBtu) |  |  |  |  | 0
Benchmark Energy Uses
Specific Electricity Use (kWh/case) |  |  |  |  | #DIV/0!
Specific Fuel (kBtu/case) |  |  |  |  | #DIV/0!
ADAPTED: 7/1/04
Sheet to be hidden
Note on A9: Accounts for efficiency losses, dehumidifying the air in fermentation and cold stabilization, and other losses unaccounted for.

## Water (hidden)
WATER CONSUMPTION: CALCULATION OF BENCHMARK WATER USE
Input Data (from input sheet) | Red | White-sweet | White-tank | White-Barrel fermented | Total
Wine fermented (Gallons) | 0 | 0 | 0 | 0 | 0
Wine production (Cases) | 0 | 0 | 0 | 0 | 0
Wine stored in barrels (Cases) | 0 | 0 | 0 | 0 | 0
Wine bottled (Cases) | 0 | 0 | 0 | 0 | 0
Water Use:
Water used in winery, crush pad, and storage areas (Gal) | 0 | 0 | 0 | 0 | 0
Water used in barrel rooms (Gal) | 0 |  |  | 0 | 0
Water used in bottling (Gal) |  |  |  |  | 0
Water used for refrigeration (Gal) | 0 | 0 | 0 | 0 | 0
Non-production uses (Gal) |  |  |  |  | 0
Total water used in wine production (Gal) |  |  |  |  | 0
Hot Water Use (part of total water use):
Hot water used in cleaning red barrels/tanks (Gal) |  |  |  |  | 0
Hot water used in cleaning and sterilizing bottling line (Gal) |  |  |  |  | 0
Total hot water use (Gal) |  |  |  |  | 0
Specific Water Use
Total Water (Gallon/case produced) |  |  |  |  | #DIV/0!
Hot Water (Gallon/case produced) |  |  |  |  | #DIV/0!
Efficiency Factor |  |  |  |  | 25.8%
Adapted: 10/19/04
Sheet to be hidden

## Weather (hidden)
Weather Data
Area | Fermentation |  | Malolactic | Stabilization
| Ambient | Roof | Ambient | Ambient | Roof
Ashland | 11.9 | 16.9 | 5.4 | 9.5 | 14.7
Astoria | 11.7 | 15.2 | 6.8 | 8.3 | 12.3
Burns | 8.1 | 12.7 | -1.3 | 4.3 | 9.7
Eugene | 11.9 | 15.7 | 5.6 | 9 | 13.4
Forest Grove | 11.8 | 15.4 | 5.2 | 9 | 13.5
Hermiston | 11.6 | 15.5 | 2.7 | 9.1 | 14.1
Hood River | 10.5 | 14.1 | 0.8 | 8.1 | 13.2
Klamath Falls | 8.7 | 13.3 | 0.3 | 5.7 | 11.1
Madras | 9.5 | 14 | 1.4 | 6.5 | 11.9
Medford | 11.3 | 15.6 | 3.8 | 8.5 | 13.9
North Bend | 12.5 | 16.5 | 8.3 | 9.5 | 14.3
Pendleton | 12.9 | 17.1 | 2.3 | 7.8 | 12.8
Portland | 12.4 | 15.9 | 6.1 | 9.1 | 13.4
Redmond | 9.4 | 14 | 0.9 | 5.7 | 11.1
Salem | 12.1 | 15.8 | 5.4 | 8.4 | 12.9